Deb Longtin, Chairman, opened the meeting at 3:05pm with introductions.  There were 6 members and 6 guests present at this meeting.

- Since there was not a quorum, the Kansas City meeting minutes were not approved.

- Deb discussed the current status of Standard 525.

- The small substation example is finished.

- Now planning for a large substation example for the next revision on the standard.

- Looking at working with C group for fiber optic and communications cable sections.

- Steve to advise Diane Watkins that D2 Working Group will not be planning to put on a tutorial in Montreal.

- Improvements to the Standard…

- Need to get a PAR initiated.  This may be done in Montreal.  Need 4 years to complete the revised document once PAR is initiated.

- We need to clarify Section 7.6 and Annex H Table H.1 for cable separation for power and control cables verses voltage and redundant cables.

- Review of the Large Station Example

- Steve had furnished a revised Plan view to Rad incorporating previous meeting comments for Rad’s use in adding proposed cable trench and conduit layout.

- Rad went through the proposed cable trench and conduit plan with the group.

- Don Wengerter recommended moving the trench for the 345kv near the deadend towers to a maximum distance from the 345kv bus.  Rad to revise accordingly.

- High voltage conduit needs to be added from the transformer tertiaries to the station service padmount transformers.

- Add conduit for the OPGW fiber cable at the deadends for the 345kv and 138kv lines.

- Rad will add grading information for showing a high point ridge down the center of the substation North to South for drainage concerns.

- Rad will add lights to structures with accompanying conduits.

- Design Parameters were reviewed by Randy.

  - Fault current is completed

  - For the battery use end of discharge value

  - Station service will be 500kva

  - Transformer fans are 480 volt

  - 120/208 volt for rest of equipment

  - 120 volt for the control house

  - 208 vac and 125 vdc dual rating for breaker motors

  - 120 volts for yard lights

- Rad to finish revising the layout and send to Steve by November 1 to review and to Deb by November 15 for distribution to the group.

- Steve to furnish Randy transformer and breaker loading information for the motors.

- Deb will send Randy and Rad information to web site.

- Comments by the Group by December 31.

- Assignments then to be started by Walt, Randy, Joe, and Diane for their previous tasks assigned for preparation prior to the Montreal meeting in May, 2010.

- The group was asked to furnish any NERC issues anticipated in the future that may affect the Standard at the Montreal meeting.

- The next working group meeting will be in Montreal in May, 2010.  The date and time will be specified later.

Respectfully submitted by

Steve Shelton

Vice-Chair, WG D2

Steve.shelton@hdrinc.com

Attendance

| First Name | Last Name | Role |
| --- | --- | --- |
| Radoslav | Barac | Member |
| Randy | Clelland | Member |
| Joe | Gravelle | Member |
| Debra | Longtin | Chair |
| Steve | Shelton | Vice-Chair |
| Brian | Wallace | Member |
| Jody | Cathay | Guest |
| Tom | Davey | Guest |
| Raj | Ghai | Guest |
| Jeff | Irving | Guest |
| Don | Wengerter | Guest |
| Alexander | Wong | Guest |