## D9 Working Group

## IEEE P1818 - Guide for the Design of Low Voltage Auxiliary Systems for Electric Power Substations

## Nashville, TN – October 7th, 2015

## Wednesday, 1:00 p.m. – 5:00 p.m.

Chair:		Hanna E. Abdallah (not present)

Vice Chair:		Joseph Gravelle

Secretary:		Radoslav Barac (not present)

Technical Editor:	Chack Haar

MEETING NOTES

- Chair has shown the IEEE Patent Slides

- Introduction of guest and members:

There were 15 of 27 members and 5 guests present at this meeting.

0 guests have requested membership.

- Review agenda and revise if required

No changes have been added to the proposed Agenda.

- Nashville meeting notes review and approvals:

- 4.6 will be removed from the standard for PAR submission; figures for transfer switches will be added on future revision.

- Standard needs to be agreed upon by May with comments incorporated.

- All assignments given today must be completed by January

- Tom Proios to review Section 4.6 by 11-1-15.

- Figure 45 to be updated by Joe Gravelle and Don Weingartner

- Reviewed Section 4.3c.

- Chuck suggested Introductory paragraph for Section 4.8

  - Joe suggested adding first two sections of 4.8 as introductory paragraph.  Change incorporated.

- Updated Table in 4.9

- Changed 4.9.1 to remove limit on number of circuits in panel.

- ‘Safety language’ removed from 4.11.1; Table 5 edited to add reference to NESC Table 125-1.

- Combined ‘e’ and ‘f’ in Section 4.7.1.

- Add Table 1 and some of original text back to 4.5.3.2.

- Brackets added for voltage drop eqs. in Section 4.4.

DC Part:

- Chuck to clean up Section 5.4.1; will add reference to IEEE 446.

- Tom to update Figure 20 with revised CAD file to show the non-continuous block at the beginning of load profile and tripping block at the end.

- 5.4.2.4 changed to add caution for equalizing voltage, not to exceed ratings of connected equipment.

- 5.6.2 edited to remove fuse/circuit breaker redundancy.

- Chuck to leave NEC 2011 references in Annex Example C.2 for now, James Purcell to update references to 2014 and send to Chuck.

- Added temperature correction factor to Annex Example C.3.

- Cautionary note to be added to Annex Example C.2 (DC Load Table)

- IEEE Std. 484 removed from Normative References.

- ‘Remote Station Terminal’ removed from definitions.

Assignments:

- Tom Proios to review 4.6.

- Whole group to review entire document. All comments to be entered in spreadsheet that Chuck will circulate.

- Chuck to incorporate changes from meeting by 20151014.

- Next Meeting - Tentative conference call to be held January 5th 2016 to determine if the standard is ready for balloting. Joe to send out link.

- Adjournment