## Slide 1: Synchrophasors: Improving Reliability & Situational Awareness
October 12, 2011
Research & Technology Management
Clifton Black

## Slide 2: Outline
What are PMUs?
PMUs - Concept & Operation
The Need for PMUs
Synchrophasor Applications
Southern Company PMU Activities
PMUs Activities in North America

## Slide 3: What are PMUs?
PMUs provide high resolution synchronized
measurements of phasor voltages and currents
They are placed at key locations like power plants and major substations

## Slide 4: Concept & Operation
Phasors
Phase Angles have a reference

## Slide 5: Concept & Operation contd.
ATTRIBUTE | SCADA | PHASOR
Measurement | Analog | Digital
Resolution | 2-4 sam./sec. | 60 sam./sec.
Observability | Steady State | Transient
Phase angle | No | Yes
Measured | ¦V¦, MW, MVAR | ¦V¦,δ, MW, MVAR, ¦δ2 – δ1¦
Synchronized | No | Yes

## Slide 6: Concept & Operation contd.
Time Synchronization
Time-skewed measurements introduce errors
Average Angle Difference ~ 10º
Average Angle Difference ~ 5º

## Slide 7: The Need for PMUs
Investigation of August 14, 2003 Blackout revealed
Lack of Wide Area Visibility
Lack of Time Synchronized Data
Inability to Monitor System Dynamic Behavior in Real-time

## Slide 8: The Need for PMUs Contd.
Wide-Area and Sub-SCADA Visibility
Time Synchronization allows Dynamics not visible in SCADA
Angular or Dynamic warning signs are usually present before major events
  Recent Major Blackouts
August 14th Angular Separation
12 Degrees
25 Degrees
45 Degrees
115 Degrees

## Slide 9: The Need for PMUs Contd.
PMUs allow us to‘see’ the dynamic behavior of the grid which models sometimes incorrectly predict.
Post Disturbance Analysis of August 10, 1996 Blackout

## Slide 10: Synchrophasor Applications
Wide-Area Visualization & Monitoring
Frequency Stability Monitoring & Trending
Voltage Monitoring & Trending
State Estimation
Oscillation Monitoring
Resource Integration
Equipment Failure Detection
Real-time Applications
Power System Model Verification
Event Analysis & Reconstruction
Equipment Failure Detection
Fault Location
Baselining Power System Performance
Load Characterization
Off-line Applications
Synchrophasors facilitates improvement in Situational Awareness, Modeling Accuracy & System Reliability

## Slide 11: Synchrophasor Applications contd.
CAISO, BPA, AEP incorporating phasor data into State Estimation tools
Entergy used phasor data to manage system separation, islanding and restoration during Gustav (2008)
CAISO & ERCOT will be using phasor data to monitor and integrate intermittent generation
SCE using phasor data for automated control of SVC for reactive power support
Phasor systems being used for WAMS in North America, Quebec, Brazil, China and Europe
A Few of the Current Implementations

## Slide 12: Southern Company PMU Locations
Plant Miller
Plant Farley
Plant Daniel
Plant Bowen
Norcross
South Hall
Plant Hatch
West McIntosh
Thallman
Plant Barry

## Slide 13: Southern Company’s PMU Architecture
HATCH
Vgθg
Veθe
Vdθd
Vbθb
Viθi
DANIEL
SOUTH HALL
BOWEN
MILLER
Phasor Data Concentrator (PDC) - Local
Regional PDC
Vfθf
NORCROSS
Vcθc
BARRY
Vaθa
FARLEY
THALMANN
Vjθj
WEST MCINTOSH
Vhθh
Local Historian
Local Applications
Local PDC and Historian facilitates flexibility, security and data accessibility

## Slide 14: Current Use of PMU data
Wide Area Monitoring and Situational Awareness – Research
Post Event Analysis & Model Validation – Transmission Planning

## Slide 15
Example of Wide-area Monitoring Tool
GAUGES: Quantify the worst performing metric
LOCATION INDICATORS: Provide information about specific locations w.r.t. the metric
TRAFFIC LIGHTS: Provide status of specific metrics across all locations
Real-time Dynamics Monitoring System (RTDMS)

## Slide 16: Synchrophasor Research
Project with PNNL: Multi-Variable Statistical Analysis –
Identifying atypical events and precursors to proactively manage the grid
AREVA PMU Project: Impact of PMU data on State Estimation & State Estimation Metrics
NEETRAC Project: Next Generation PMUs/Evaluation
CEATI: Prediction of Power System Instability based on PMU data: Utilizing the Region of Stability Existence (ROSE) Approach.
Provide Operators with fast and accurate solutions in order to predict system instability and prevent wide-spread blackouts using PMU data.

## Slide 17: Demonstration Project w/ GaTech
Distributed State Estimator, Generator Parameter Estimation and Stability Monitoring
  Distributed State Estimator for two substation subsystem
  Develop Generator parameter Estimator for a generating unit
  Develop transient stability monitoring system for generating plant

## Slide 18: PMUs in North America

## Slide 19: PMU Activities in North America
North America
  North American Synchrophasor Initiative (NASPI) www.naspi.org
  SPDC evolving to regional PDCs
  PhasorGateway – Communications & Traffic Management Infrastructure
  Tremendous boost from ARRA funding
NASPI Structure

## Slide 20: Where Are We Going?
1. Angle/Freq. Monitoring
12. Post-mortem Analysis
2. Voltage Stability Monitoring
5. State Estimation (Improv.)
13. Model Benchmarking;
Parameter Estimation
16. DG/IPP Applications
11. Power system restoration
10. Congestion management
14. Model Benchmarking; Parameter Estimation
15. Planned Power System
Separation
6. State Estimation
(Boundary Conditions)
7. State Measurement (linear)
4. Real-Time Control
9. Adaptive Protection
8. WA Stabilization (WA-PSS)
Necessary
Additional Benefits
More Investigation
Role of PMUs
1-3 Years
3-5 Years
> 5 Years
Recommended Industry Deployment Roadmap
3. Thermal Overload Monitoring
CIEE Report

## Slide 21: SGIG PMU Projects
Project Lead | # of PMU (Stations) | Key Applications
ISO New England | 30 | Real-time situational awareness, Congestion management
New York ISO | 39 | Real-time situational awareness, Voltage monitoring and control Communications system
PJM Interconnection | 80+ | Real-time situational awareness including trending, Oscillation detection, Islanding detection
Midwest ISO | 150+ | Real-time situational awareness, Voltage monitoring Renewable integration, Congestion management, State estimation, Oscillation monitoring, EMS alarms
Western Electric Coordinating Council | 250+ | Wide-area real-time situational awareness and visualization, Alarming, Oscillation monitoring, Voltage monitoring, Renewable integration, Congestion management, Automatic controls, Power system performance analysis, System-wide model validation, Post-event analysis
Entergy Services | 18 | Increase grid monitoring, train and educate grid operators and engineers on phasor technology
Duke Energy | 102 | Wide-area real-time situational awareness, enhanced state estimator and Renewables integration

## Slide 22: What Do We Need Now?
Demarcation where currents tools end and PMU tools begin
Development and Deployment of Applications
Practical tools for Operators
Actionable Information
‘Killer Apps’
Knowledge/Experience from SGIG implementations
More Research

## Slide 23: Questions