## Slide 1: PV Solar Projects

## Slide 2: PV Solar Installations 2010-2013

## Slide 3: PV Solar Exceeds 10 GW in 2013
The 2012 total US electric generation capacity was 1,063 GW.
The main energy sources include:
Thermal/Fossil 776 GW
Nuclear 102 GW
Hydropower 79 GW
Wind 59 GW

## Slide 4
United States Electric Grid; the largest interconnected
machine on earth

## Slide 5: Location, Location
PV Solar Project Locations

## Slide 6: PV Solar Installed Cost Dropping

## Slide 7: PV Photo-Voltaic Cell
Russell Ohl 1940

## Slide 8: PV Solar Review
Modules

## Slide 9: PV module string

## Slide 10: PV string combiner box

## Slide 11: Combiner Box

## Slide 12: Inverters

## Slide 13: Collector system

## Slide 14: Interconnect

## Slide 15: Foothills 34 MW
177,840 polycrystalline 295 W PV modules
20 modules per string; 8,892 strings
56 inverters; 20 - 1 MW & 36 - 0.5 MW
19 PCS skids with 2 MW of inverters & a 2.2 MVA transformer
12.47 kV Collector
7.5 MVAR Capacitors
69 kV Interconnect

## Slide 16: Victor Phelan 17.5 MW
-78,624 modules
-3,744 strings
-35 - 500 kW inverters
-10 PCS skids
-34.5 kV Collector
-34.5 kV Interconnect

## Slide 17: Azalea 7.5 MW Davisboro, Ga
-31,000 modules
-9 PCS skids
-9 months start to finish
-13.8 kV collector system
-46 kV interconnect

## Slide 18: Indy Solar I,II,III
Started all 3 projects June 15 2013; completed December 15 2013.
Indy I & II were each 10 MW; had 46,284 modules; 2,436 strings; 14 inverters & 7 PCS’s
Indy III was 8.64 MW; had 39,672 modules; 2,088 modules, 12 inverters & 5 PCS’s

## Slide 19: Copper Mountain Solar 3 250 MW
-1,132,800 modules
-56,640 strings
-255 - 1 MW inverters
-34.5 kV collector system
-525 kV interconnection
-Currently under construction

## Slide 20
Some Assembly Required

## Slide 21
Lots of Trenches

## Slide 22
Installing the PCS

## Slide 23
Lots of wiring

## Slide 24
Neither snow nor rain…..

## Slide 25: North American Grid Codes
Nice thought but we’re not there yet.

## Slide 26: Interconnection Rules
Balancing Authorities
ISOs RTOs
State Energy Commissions

## Slide 27: Point of Common Contention
IEEE 1547 says the DR (10 MVA or less) shall not actively regulate the voltage at the PCC & shall not cause the Area EPS service voltage at other local EPS’s to go outside C84.1 Range A.
C84.1 Range service voltage maximum 105% nominal; minimum 97.5% nominal

## Slide 28: NERC Requirements
FERC Federal Energy Regulatory Commission has jurisdiction over interstate electricity sales & wholesale electric rates, appointed NERC North American Electric Reliability Corporation as the Electric Reliability Organization in US.
NERC’s mission is ensure the reliability of the bulk power system; their policies are now standards that are enforceable on bulk power system operators by financial penalties
FERC orders affect large & small generator interconnect agreements with a 4 step review process; scoping, feasibility, system impact and facility studies
FERC interconnect order 661-A for wind generators >20MW was the genesis of LVRT, reactive power & power factor requirements
NERC standards have implemented these orders for all generation on the bulk power system under their Voltage and Reactive (VAR) standard and 024-1 standard

## Slide 29: NERC 024-1 Voltage Ride Through

## Slide 30: NERC 024-1 Frequency Limits

## Slide 31: Conflict in application of standards
Shall not actively regulate the voltage at the PCC & shall not cause the Area EPS service voltage at other local EPS’s to go outside C84.1 Range A.
C84.1 Range service voltage maximum 105% nominal; minimum 97.5% nominal
Primary consideration is protection
Overvoltage relay (59) settings very restrictive
Primary consideration is reliability
Overvoltage relay (59) settings relaxed

## Slide 32: The Results
Persistent overvoltage trips where restrictive relay settings were employed or no voltage control (by VAR production or absorption) allowed. Precisely the problem that FERC & NERC wanted to resolve

## Slide 33: Success, Well Improvement

## Slide 34: A variation on the same theme…unity PF operation & overvoltage trips at POI or inverter

## Slide 35
Successful resolution by
allowing inverters to absorb
VARS the overvoltage issues
were resolved

## Slide 36: FERC 661A Reactive Power Requirements
Provide reactive power to have a +/- 0.95 PF at POI (Point of Interconnect) or PCC
Synchronous Generator reactive
capability curve
Synchronous machine considering
minimum power limits
Typical PV Inverter reactive capability

## Slide 37: PV Inverter Reactive Limitations
VARS are not imaginary. So where are they
going to coming from and what kind do
they need to be?
Could be
capacitors, static
Could be STATCOM,
dynamic

## Slide 38: Project Reactive Power Example
40 MVA HV XFMR
37.2 MW OUTPUT
12.23 MVAR FOR 0.95 PF @ POI
69 KV HV
INVERTERS REACTIVE OUTPUT 12.58 MVAR
COLLECTOR SYSTEM LOSSES -2 MVAR
HV XFMR REACTIVE LOSSES -4 MVAR
CAP BANK REACTIVE OUTPUT (3@2) 6 MVAR
NET REACTIVE OUTPUT 12.58 MVAR

## Slide 39: Collector System Reactive Power Control

## Slide 40: Closed Loop Reactive Power Control
PF Control
Overall Schematic

## Slide 41: Volt / VAR Control
VARS circulate between buses of unequal voltage magnitude; when the system voltage
is low more VARS are needed to be generated, when the system voltage is high VARS
may need to be absorbed.

## Slide 42: Can you get there from here?
Voltage Array (% VRef) |  | VAr Array (% VArAval) | 
V1 | 97 | Q1 | 50
V2 | 99 | Q2 | 0
V3 | 101 | Q3 | 0
V4 | 103 | Q4 | 50
Voltage and VARS are at the PCC (POI)
not in your plant. VARS flow from high
voltage (p.u.) to low voltage but you can
only go to 105%
Typical setpoints from Utility

## Slide 43: Dead band or Hysteresis for Stability
Typically +/-1 to 4 %
Time frame variable depending on
control system response time, anti-
islanding controls, static or dynamic
reactive power source utilization

## Slide 44: Example of Volt/VAR Control

## Slide 45: 11-11-13 Davisboro; Clear weather

## Slide 46: 11-09-13 Davisboro; Overcast weather

## Slide 47: Ramp Rates
Establishing the use of ramp rates for moving from one
output level to another will help avoid sharp transitions
and the consequential power quality problems of
voltage spikes or dips, harmonics, and oscillations.
For large solar installations the ramp rate also prevents a system frequency deviation due
to a larger generation change.
ERCOT, CAISO,PREPA & others have required a ramp rate maximum of 10% of nameplate
MW rating
Standard ramp rate
10% ramp rate

## Slide 48: 1.2 MW PV On Island with 4.7 MW Load
Ramp rate limited 360 kw/min @ startup &
shutdown, 40-60 kw/sec operating
In this event a 35 kw/sec ramp produced a
0.12 hz frequency increase
With increased PV penetration levels ramp rates are becoming an issue.

## Slide 49
Collector Circuit Relaying

## Slide 50: That Can’t Be Right, Can It?

## Slide 51: Interesting Weather Trivia