## Slide 1: 2017 NEC Revisions
Presented to: IEEE-IAS (Atlanta)
Presented by:
Michael D. Seal, P.E.
2000A
400A
1200A
1600A

## Slide 2: 2014 NEC Article 240.87
240.87 Arc Energy Reduction. Where the highest continuous current trip setting for which the actual overcurrent device installed in a circuit breaker is rated or can be adjusted is 1200 A or higher, 240.87(A) and (B) shall apply.
(A) Documentation. Documentation shall be available to those authorized to design, install, operate, or inspect the installation as to the location of the circuit breaker(s).
(B) Method to Reduce Clearing Time. One of the following or approved equivalent means shall be provided:
(1) Zone-selective interlocking
(2) Differential relaying
(3) Energy-reducing maintenance switching with local status indicator
(4) Energy-reducing active arc flash mitigation system
(5) An approved equivalent means

## Slide 3: 2017 NEC Article 240.87
240.87 Arc Energy Reduction. Where the highest continuous current trip setting for which the actual overcurrent device installed in a circuit breaker is rated or can be adjusted is 1200 A or higher, 240.87(A) and (B) shall apply.
(A) Documentation. Documentation shall be available to those authorized to design, install, operate, or inspect the installation as to the location of the circuit breaker(s).
(B) Method to Reduce Clearing Time. One of the following means shall be provided:
(1) Zone-selective interlocking
(2) Differential relaying
(3) Energy-reducing maintenance switching with local status indicator
(4) Energy-reducing active arc flash mitigation system
(5) An Instantaneous trip setting that is less than the available arcing current
(6) An Instantaneous override that is less than the available arcing current
(7) An approved equivalent means

## Slide 4: Zone Selective Interlocking (ZSI)
To further illustrate the various solutions available the attached single line will be used.
Per the code requirement the 2000A, 1200A and 1600A circuits will require arc energy reduction as they are rated 1200A or more.
The options are:
    Zone-selective interlocking
2000A
400A
1200A
1600A
Blocking signals

## Slide 5: Differential relaying - basics
To further illustrate the various solutions available the attached single line will be used.
Per the code requirement the 2000A, 1200A and 1600A circuits will require arc energy reduction as they are rated 1200A or more.
The options are:
    Zone-selective interlocking
    Differential relaying
2000A
400A
1200A
1600A
87B
I1
I4
I3
I2
Protected zone
Outside protected zone
Outside protected zone
Outside protected zone

## Slide 6: Maintenance Switch
To further illustrate the various solutions available the attached single line will be used.
Per the code requirement the 2000A, 1200A and 1600A circuits will require arc energy reduction as they are rated 1200A or more.
The options are:
    Zone-selective interlocking
    Differential relaying
    Energy-reducing maintenance switching with local status indicator
2000A
400A
1200A
1600A

## Slide 7: 2017 NEC Article 240.87
240.87 Arc Energy Reduction. Where the highest continuous current trip setting for which the actual overcurrent device installed in a circuit breaker is rated or can be adjusted is 1200 A or higher, 240.87(A) and (B) shall apply.
(A) Documentation. Documentation shall be available to those authorized to design, install, operate, or inspect the installation as to the location of the circuit breaker(s).
(B) Method to Reduce Clearing Time. One of the following means shall be provided:
(1) Zone-selective interlocking
(2) Differential relaying
(3) Energy-reducing maintenance switching with local status indicator
(4) Energy-reducing active arc flash mitigation system
(5) An Instantaneous trip setting that is less than the available arcing current
(6) An Instantaneous override that is less than the available arcing current
(7) An approved equivalent means

## Slide 8: Relationship of arcing current to Ibf at specific voltages

## Slide 9: 2017 NEC Article 240.67
240.67 Arc Energy Reduction. Where fuses rated 1200A or higher are installed, 240.67(A) and (B) shall apply. This requirement shall become effective January 1, 2020.
Documentation. Documentation shall be available to those authorized to design, install, operate, or inspect the installation as to the location of the fuses.
(B) Method to Reduce Clearing Time. A fuse shall have a clearing time of 0.07 seconds or less at the available arcing current, or one of the following means shall be provided:
(1) Differential relaying
(2) Energy-reducing maintenance switching with local status indicator
(3) Energy-reducing active arc flash mitigation system
(4) An approved equivalent means

## Slide 10: Fuse Time Current Curve (TCC)

## Slide 15: Article 430.99

## Slide 16
.
Questions ??

## Slide 17: NEC Article 230.95 (C)
230.95 (C). Performance Testing. The ground-fault protection system shall be performance tested when first installed on site. This testing shall be conducted by a qualified person using a test process of primary current injection, in accordance with the instructions that shall be provided with the equipment. A written record of this testing shall be made and shall be available to the authority having jurisdiction.

## Slide 18: NEC Article 110.14 (D)
110.14 (D). Installation. Where a tightening torque is indicated as a numeric value on equipment or in installation instructions provided by the manufacturer, a calibrated torque tool shall be used to achieve the indicated torque value, unless the equipment manufacturer has provided installation instructions for an alternative method of achieving the required torque.