## Source
Source Sequence Impedances
Primary LL kV | R pos | X pos | R zero | X zero
| Ω | Ω | Ω | Ω
115 | 1.48 | 11.6 | 4.73 | 21.2 |  | x
Source Operating Voltages
V AB |  | V BC |  | V CA
Magnitude | Angle | Magnitude | Angle | Magnitude | Angle
(Volts) | (Degrees) | (Volts) | (Degrees) | (Volts) | (Degrees)
115000 | 30 | 115000 | -90 | 115000 | 150 | x

## Sub Xfm
Substation Three-PhaseTransformer
| Connectiion | From | To | Rated | % Impedance |  | Rated Voltages
|  | Node | Node | kVA | R | X | High | Low
T-Sub | Delta-Grd. Y | 700 | 701 | 5000 | 1 | 8 | 115 kV | 14.4 kV (LG)
|  | High Side | Low Side
| High Side Taps | kV(LL) | kV(LL)
| A | 120.75 | 24.9
| B | 117.875 | 24.9
| C | 115 | 24.9
Set At | D | 112.125 | 24.9
| E | 109.25 | 24.9

## Construction Code
Construction Code | Type |  |  | x + j y Coordinates
|  | Position 1 |  | Position 2 |  | Position 3 |  | Neutral |  | Units
|  | x | y | x | y | x | y | x | y
500 | Three-phase OH, 4 wire | 0 | 29 | 2.5 | 29 | 7 | 29 | 4 | 25 | ft
505 | Three-phase OH, 3 wire | 0 | 29 | 2.5 | 29 | 7 | 29 |  |  | ft
510 | Two-phase OH, 3 wire | 0 | 29 | 7 | 29 |  |  | 4 |  | ft
515 | Two-phase OH, 2 wire | 0 | 29 | 7 | 29 |  |  |  |  | ft
520 | Single-phase OH, 2 wire | 0 | 30 |  |  |  |  | 0.5 | 25 | ft
525 | Three-phase UG, 3 cable, +1 neutral | 0 | -40 | 6 | -40 | 12 | -40 | 18 | -40 | in
530 | Three-phase UG, 3 cable | 0 | -40 | 6 | -40 | 12 | -40 |  |  | in
535 | Two-phase UG, 2 cable + 1 neutral | 0 | -40 | 6 | -40 |  |  | 12 | -40 | in
540 | Two-phase UG, 2 cable | 0 | -40 | 6 | -40 |  |  |  |  | in
545 | Single-phase UG, 1 cable +1 neutral | 0 | -40 |  |  |  |  | 6 | -40 | in
550 | Single-phase UG, 1 cable | 0 | -40 | [6 empty] | in
555 | Triplex OH | 0 | 25 | 0.0445 | 25 |  |  | 0.02225 | 24.9657 | ft
560 | Quadraplex, OH | 0 | 25 | 0.02225 | 25.0385 | 0.0445 | 25 | 0.02225 | 24.9657 | ft
565 | Three-phase OH, +1, parallel 1 | 0 | 33 | 2.5 | 33 | 7 | 33 | 4 | 25 | ft
570 | Three-phase OH, parallel 2 | 0 | 29 | 2.5 | 29 | 7 | 29 |  |  | ft
575 | Three-phase, UG, 3 cable, parallel 1 | 0 | -40 | 6 | -40 | 12 | -40 | 18 | -40 | in
580 | Three-phase, UG, 3 cable, parallel 2 | 0 | -46 | 6 | -46 | 12 | -46 |  |  | in
2

## Config. Codes
Configuration Codes
Config. Code | Const. Code | Phasing | Phase Cond. | Cable Neut. | Neutral Cond
400 | 500 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1
405 | 505 | b-a-c | #2 ACSR 6/1 | none | none
410 | 510 | b-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1
415 | 515 | b-c | #2 ACSR 6/1 | none | none
420 | 520 | a-n | #2 ACSR 6/1 | none | #2 ACSR 6/1
425 | 525 | a-b-c-n | 2/0 AA CN | 1/3 neutral | 1/0 CU
430 | 530 | a-b-c | 1/0 AA CN | 1/3 neutral | none
435 | 535 | b-c-n | 1/0 AA TS | Tape | 1/0 CU
440 | 540 | b-c | 1/0 AA CN | Full neutral | none
445 | 545 | b-n | 2/0 AA CN | 1/3 neutral | 1/0 CU
450 | 550 | a-n | 1/0 AA CN | Full neutral | none
455 | 555 | 1-2-n | 2/0 AA 7s | none | 2/0 ACSR 6/1
460 | 560 | 1-2-3-n | 2/0 AA 7s | none | 2/0 ACSR 6/1
465 | 565 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1
470 | 570 | b-a-c-n | 2/0 ACSR 6/1 | none | none
475 | 575 | b-a-c-n | 2/0 AA CN | 1/3 neutral | 1/0 CU
480 | 580 | b-a-c-n | 1/0 AA CN | 1/3 neutral | none

## Config Z&Y
Configuration codes Zabc and Yabc matrices
| R | X | R | X | R | X | B | B | B
| Ω/mile | Ω/mile | Ω/mile | Ω/mile | Ω/mile | Ω/mile | μS/mile | μS/mile | μS/mile
400 | 1.3368 | 1.3343 | 0.2101 | 0.5779 | 0.213 | 0.5015 | 5.335 | -1.5313 | -0.9943
| 0.2101 | 0.5779 | 1.3238 | 1.3569 | 0.2066 | 0.4591 | -1.5313 | 5.0979 | -0.6212
| 0.213 | 0.5015 | 0.2066 | 0.4591 | 1.3294 | 1.3471 | -0.9943 | -0.6212 | 4.888
405 | 1.7853 | 1.6273 | 0.0953 | 0.8515 | 0.0953 | 0.7802 | 4.8839 | -1.5406 | -1.0899
| 0.0953 | 0.8515 | 1.7853 | 1.6273 | 0.0953 | 0.7266 | -1.5406 | 4.7351 | -0.7207
| 0.0953 | 0.7802 | 0.0953 | 0.7266 | 1.7853 | 1.6273 | -1.0899 | -0.7207 | 4.4924
410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 1.3249 | 1.3557 | 0.2067 | 0.4591 | 0 | 1.544 | -1.0136
| 0 | 0 | 0.2067 | 0.4591 | 1.3295 | 1.3459 | 0 | -1.0136 | 4.5935
415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 1.7853 | 1.6273 | 0.0953 | 0.7266 | 0 | 4.2491 | -1.0645
| 0 | 0 | 0.0953 | 0.7266 | 1.7853 | 1.6273 | 0 | -1.0645 | 4.2491
420 | 1.9217 | 1.4206 | 0 | 0 | 0 | 0 | 4.3159 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
425 | 1.134 | 0.6452 | 0.319 | 0.1768 | 0.2786 | 0.0849 | 74.6244 | 0 | 0
| 0.319 | 0.1768 | 1.1254 | 0.5893 | 0.2992 | 0.1325 | 0 | 74.6244 | 0
| 0.2786 | 0.0849 | 0.2992 | 0.1325 | 1.0995 | 0.5516 | 0 | 0 | 74.6244
430 | 1.5208 | 0.7523 | 0.5195 | 0.2778 | 0.4922 | 0.2159 | 67.03 | 0 | 0
| 0.5195 | 0.2778 | 1.5327 | 0.7165 | 0.5195 | 0.2778 | 0 | 67.03 | 0
| 0.4922 | 0.2159 | 0.5195 | 0.2778 | 1.5208 | 0.7523 | 0 | 0 | 67.03
435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 1.3197 | 0.8082 | 0.3261 | 0.3056 | 0 | 89.3179 | 0
| 0 | 0 | 0.3261 | 0.3056 | 1.3212 | 0.7198 | 0 | 0 | 89.3179
440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 1.4094 | 0.445 | 0.3508 | 0.012 | 0 | 77.8502 | 0
| 0 | 0 | 0.3508 | 0.012 | 1.4094 | 0.445 | 0 | 0 | 77.8502
445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 1.1511 | 0.6615 | 0 | 0 | 0 | 74.6244 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
450 | 1.59 | 0.5665 | 0 | 0 | 0 | 0 | 74.7048 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
455 | 1.2542 | 0.6032 | 0.4857 | 0.4492 | 0 | 0 | 25.4969 | -10.217 | 0
| 0.4857 | 0.4492 | 1.2551 | 0.6015 | 0 | 0 | -10.217 | 25.826 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
460 | 1.2542 | 0.6032 | 0.4621 | 0.4935 | 0.4857 | 0.4492 | 20.9844 | -8.3159 | -5.5804
| 0.4621 | 0.4935 | 1.2092 | 0.6894 | 0.4625 | 0.4938 | -8.3159 | 18.1946 | -8.3159
| 0.4857 | 0.4492 | 0.4625 | 0.4938 | 1.2551 | 0.6015 | -5.5804 | -8.3159 | 20.9844
465 self | 1.3081 | 1.3837 | 0.1861 | 0.6204 | 0.1871 | 0.5473 | 5.5021 | -1.335 | -0.8393
| 0.1861 | 0.6204 | 1.3042 | 1.3907 | 0.1851 | 0.4972 | -1.335 | 5.3369 | -0.4648
| 0.1871 | 0.5473 | 0.1851 | 0.4972 | 1.3061 | 1.3873 | -0.8393 | -0.4648 | 5.1054
465 mutual to 470 | 0.2016 | 0.5357 | 0.1957 | 0.5262 | 0.1983 | 0.492 | -0.7185 | -0.6 | -0.4981
| 0.1994 | 0.5196 | 0.1936 | 0.5499 | 0.1936 | 0.4603 | -0.5878 | -0.8822 | -0.3087
| 0.2005 | 0.4881 | 0.1946 | 0.4631 | 0.1972 | 0.5436 | -0.4833 | -0.3084 | -1.0364
470 mutual to 465 | 0.2016 | 0.5357 | 0.1994 | 0.5196 | 0.2005 | 0.4881 | -0.7185 | -0.5878 | -0.4833
| 0.1957 | 0.5262 | 0.1936 | 0.5499 | 0.1946 | 0.4631 | -0.6 | -0.8822 | -0.3084
| 0.1983 | 0.492 | 0.1936 | 0.4603 | 0.1972 | 0.5436 | -0.4981 | -0.3087 | -1.0364
470 self | 1.1119 | 1.3179 | 0.2102 | 0.5778 | 0.2132 | 0.5014 | 5.7553 | -1.2748 | -0.7303
| 0.2102 | 0.5778 | 1.0989 | 1.3405 | 0.2067 | 0.4591 | -1.2748 | 5.534 | -0.3668
| 0.2132 | 0.5014 | 0.2067 | 0.4591 | 1.1045 | 1.3307 | -0.7303 | -0.3668 | 5.3384
470 mutual to OH-1 | 0.2016 | 0.5357 | 0.1994 | 0.5196 | 0.2005 | 0.4881 | -0.5493 | -0.4666 | -0.3883
| 0.1957 | 0.5262 | 0.1936 | 0.5499 | 0.1946 | 0.4631 | -0.4745 | -0.654 | -0.2658
| 0.1983 | 0.492 | 0.1961 | 0.4603 | 0.1972 | 0.5436 | -0.3974 | -0.2656 | -0.7538
475 self | 1.0586 | 0.5105 | 0.2539 | 0.0952 | 0.2329 | 0.0664 | 74.6004 | 0 | 0
| 0.2539 | 0.0952 | 1.0731 | 0.5595 | 0.2125 | 0.017 | 0 | 74.6004 | 0
| 0.2329 | 0.0664 | 0.2125 | 0.017 | 1.0365 | 0.4958 | 0 | 0 | 74.6004
475 mutual to UG-2 | 0.2476 | 0.0829 | 0.2419 | 0.0662 | 0.2264 | 0.0453 | 0 | 0 | 0
| 0.2428 | 0.0685 | 0.2606 | 0.1292 | 0.2139 | 0.0214 | 0 | 0 | 0
| 0.2222 | 0.0402 | 0.2088 | 0.0143 | 0.2283 | 0.0757 | 0 | 0 | 0
480 self | 1.255 | 0.5528 | 0.2521 | 0.119 | 0.2368 | 0.0984 | 67.0081 | 0 | 0
| 0.2521 | 0.0119 | 1.2653 | 0.597 | 0.218 | 0.0438 | 0 | 67.0081 | 0
| 0.2368 | 0.0984 | 0.218 | 0.0438 | 1.2376 | 0.5528 | 0 | 0 | 67.0081
480 mutual to UG-1 | 0.2476 | 0.0829 | 0.2428 | 0.0685 | 0.2222 | 0.0402 | 0 | 0 | 0
| 0.2419 | 0.0662 | 0.2606 | 0.1292 | 0.2088 | 0.0143 | 0 | 0 | 0
| 0.2264 | 0.0453 | 0.2139 | 0.0214 | 0.2283 | 0.0757 | 0 | 0 | 0

## Conductor Data
Conductor Data | Type | Resistance 50° | Diameter | GMR | Rating
|  | Ohms/mile | Inches | Ft. | Amps
1,000,000 CM | AA | 0.105 | 1.15 | 0.0368 | 698
556500 CM | ACSR | 0.186 | 0.927 | 0.0311 | 730
500,000 CM | AA | 0.206 | 0.813 | 0.026 | 483
336,400 CM | ACSR | 0.306 | 0.721 | 0.0244 | 530
250,000 CM | AA | 0.41 | 0.567 | 0.0171 | 329
#4/0 | ACSR | 0.592 | 0.563 | 0.00814 | 340
#2/0 | AA | 0.769 | 0.414 | 0.0125 | 230
#2/0 | ACSR | 0.895 | 0.447 | 0.0051 | 270
#1/0 | AA | 0.97 | 0.368 | 0.0111 | 202
#1/0 | ACSR | 1.12 | 0.398 | 0.0045 | 230
#1/0 | CU | 0.607 | 0.368 | 0.0111 | 310
#2 | AA | 1.54 | 0.292 | 0.0088 | 156
#2 6/1 | ACSR | 1.69 | 0.316 | 0.0042 | 180
#4 7/1 | ACSR | 2.55 | 0.257 | 0.0045 | 140
#10 | CU | 5.903 | 0.102 | 0.0033 | 80
#12 | CU | 9.375 | 0.081 | 0.0026 | 75
#14 | CU | 14.872 | 0.064 | 0.0021 | 20
AA = All Aluminum
ACSR = Aluminum Conductor Steel Reinforced
CU = Copper

## Cable Data
Concentric Neutral Cable
Conductor | Neutral | Nominal Dia. | Nominal Dia. | Copper | Nominal Dia. | Nominal Dia.
Size |  | Over Insulation | Over Insulation Screen | Neutral | Over Strands | Over Jacket
Awg |  | Inch | Inch | No. x Awg | Inch | Inch
1/0 AA | One Third |  | 0.93 | 6 x 14 | 1.06 | 1.23
1/0 AA | Full | 0.85 | 0.93 | 16 x 14 | 1.06 | 1.23
2/0 AA | One Third | 0.9 | 0.97 | 7 x 14 | 1.1 | 1.29
Tape Shielded Cable
Conductor | No. of | Nominal Dia. | Nominal Dia. | Nominal Dia. | Jacket | Tape
Size | Wires | Over Insulation | Over Tape Sheld | Over Jacket | Thickness | Thickness
Awg |  | Inch | Inch | Inch | Mils | Mils
1/0 AA | 19 | 0.82 | 0.88 | 1.06 | 80 | 5

## Lines
Dsignation | From | To | Length (ft.) | Phasing | Phase Cond. | Cable Neut. | Neutral | Cons. | Config.
[7 empty] | Conductor | Code | Code
UG-1 parallel with UG-2 | 702 | 713 | 3000 | b-a-c-n | 2/0 AA CN | 1/3 neutral | 1/0 CU | 575 | 475
UG-2 parallel with UG-1 | 702 | 703 | 3000 | b-a-c-n | 1/0 AA CN | 1/3 neutral | none | 580 | 480
OH-1 parallel with OH-2 | 713 | 717 | 15000 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 565 | 465
OH-2 parallel with OH-1 | 703 | 704 | 15000 | b-a-c-n | 2/0 ACSR 6/1 | none | none | 570 | 470
OH-6 | 717 | 727 | 20000 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-7 | 727 | 731 | 17750 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-8 | 731 | 735 | 3000 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-9 | 736 | 741 | 10000 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-10 | 741 | 742 | 3000 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-11 | 742 | 744 | 30000 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-12 | 745 | 746 | 850 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-13 | 746 | 747 | 20000 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-14 | 747 | 749 | 520 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-15 | 749 | 750 | 23000 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-16 | 749 | 752 | 35000 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-17 | 752 | 753 | 500 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-18 | 754 | 755 | 5000 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-19 | 753 | 757 | 4900 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-20 | 757 | 758 | 1600 | a-n | #2 ACSR 6/1 | none | #2 ACSR 6/1 | 520 | 420
OH-21 | 757 | 760 | 5800 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-22 | 760 | 765 | 4500 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-23 | 765 | 771 | 860 | b-a-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 500 | 400
OH-26 | 767 | 768 | 5200 | a-b-c | #2 ACSR 6/1 | none | none | 505 | 405
UG-5 | 760 | 761 | 1500 | a-b-c-n | 2/0 AA CN | 1/3 neutral | 1/0 CU | 525 | 425
OH-25 | 761 | 763 | 2000 | a-b-c-n | #2 ACSR 6/1 | none | #2 ACSR 6/1 | 500 | 400
OH-24 | 736 | 737 | 17000 | b-c-n | 1/0 ACSR 6/1 | none | 1/0 ACSR 6/1 | 510 | 410
UG-4 | 737 | 738 | 5000 | b-c-n | 1/0 AA TS | Tape | 1/0 CU | 535 | 435
UG-8 | 706 | 707 | 2500 | a-b-c | 1/0 AA CN | 1/3 neutral | none | 530 | 430
UG-9 | 707 | 709 | 2500 | b-c | 1/0 AA CN | Full neutral | none | 540 | 440
OH-5 | 709 | 711 | 2500 | b-c | #2 ACSR 6/1 | none | none | 515 | 415
UG-7 | 718 | 719 | 5280 | a-n | 1/0 AA CN | Full neutral | none | 550 | 450
UG-10 | 727 | 729 | 1000 | b-n | 2/0 AA CN | 1/3 neutral | 1/0 CU | 545 | 445
SEC-1 | 720 | 724 | 150 | 1-2-n | 2/0 AA 7s | none | 2/0 ACSR 6/1 | 555 | 455
SEC-2 | 724 | 725 | 150 | 1-2-n | 2/0 AA 7s | none | 2/0 ACSR 6/1 | 555 | 455
SEC-3 | 725 | 726 | 150 | 1-2-n | 2/0 AA 7s | none | 2/0 ACSR 6/1 | 555 | 455
SEC-4 | 720 | 721 | 150 | 1-2-n | 2/0 AA 7s | none | 2/0 ACSR 6/1 | 555 | 455
SEC-5 | 721 | 722 | 150 | 1-2-n | 2/0 AA 7s | none | 2/0 ACSR 6/1 | 555 | 455
SEC-6 | 722 | 723 | 150 | 1-2-n | 2/0 AA 7s | none | 2/0 ACSR 6/1 | 555 | 455
SEC-7 | 732 | 733 | 150 | 1-2-3-n | 2/0 AA 7s | none | 2/0 ACSR 6/1 | 560 | 460
SEC-8 | 733 | 734 | 150 | 1-2-3-n | 2/0 AA 7s | none | 2/0 ACSR 6/1 | 560 | 460

## Xfm Banks
Three-Phase Banks with Three Single-Phase Transformers
|  |  |  | Rated Voltages (kV) |  | Phase-a(ab) | Phase-b(bc) | Phase-c(ca)
Xfm No. | Connection | From | To | Primary | Secondary | kVA | kVA | kVA
T1 | Grd. Y - Grd. Y | 713 | 714 | 14.4 | 0.12 | 100 | 100 | 100
T3 | Grd. Y - Delta | 727 | 728 | 14.4 | 0.24 | 25 | 10 | 10
T4 | Ungrd. Y - Delta CT | 731 | 732 | 14.4 | 0.24 | 50 CT | 25 | 25
T7 | Ungrd. Y - Delta | 742 | 743 | 14.4 | 0.24 | 100 | 100 | 100
T8 | Ungrd. Y -Delta CT | 747 | 748 | 14.4 | 0.24 | 25 | 50 CT | 25
T11 | Delta - Grd. Y | 755 | 756 | 34.5 | 0.12 | 100 | 100 | 100
T22 | Delta - Delta CT | 768 | 769 | 12.47 | 0.24 | 25 | 50 CT | 25
T24 | Grd. Y - Delta | 714 | 716 | 0.12 | 0.48 | 10 | 10 | 10
Open Three-Phase Banks with Two Single-Phase Transformers
T5 | Open Grd. Y - Delta | 737 | 740 | 14.4 | 0.24 |  | 50 | 50
T6 | Open Grd. Y - Delta CT | 738 | 739 | 14.4 | 0.24 |  | 50 CT | 50
T13 | Open Delta - Delta | 761 | 762 | 24.9 | 0.48 | 50 |  | 50
T14 | Open Delta - Open Delta CT | 763 | 764 | 24.9 | 0.24 | 25 |  | 50 CT
T19 | Open Delta - Grd. Y | 771 | 772 | 24.9 | 0.12 |  | 100 | 100
Single-Phase Banks
T2 | Grd. Y - Delta CT | 719 | 720 | 14.4 | 0.24 | 100 CT
T12 | Grd. Y - Delta | 758 | 759 | 14.4 | 0.24 | 50
T16 | Delta - Delta | 707 | 708 | 12.47 | 0.24 | 100
T17 | Delta - Grd. Y | 709 | 710 | 12.47 | 0.12 |  |  | 100
T18 | Delat Delta CT | 711 | 712 | 12.47 | 0.24 |  | 100 CT
T23 | Grd. Y - Delta | 729 | 730 | 14.4 | 0.24 |  | 100
Three-Phase Banks with One Three-Phase Transformer
T9 | Delta - Delta | 750 | 751 | 24.9 | 0.48 | 500
T10 | Delta - Grd. Y | 753 | 754 | 24.9 | 34.5 | 500
T15 | Delta - Delta | 768 | 770 | 12.47 | 0.24 | 500
T20 | Grd. Y - Delta | 765 | 766 | 24.9 | 12.47 | 500
T21 | Grd. Y - Delta | 704 | 705 | 24.9 | 12.47 | 500
Transformer Phase Shifts
Step Up Transformers : + 30 degree phase shift
Step Down Transformers: -30 degree phase shift

## Xfm Z
All impedances are in % based upon rated high and low side voltages
Single-Phase Transformer Impedance
Rating | % Impedance
kVA | R | X | Z | X/R
100 | 1 | 2.1 | 2.3259 | 2.1
50 | 1.1 | 1.8 | 2.1095 | 1.6364
25 | 1.2 | 1.7 | 2.0809 | 1.4167
10 | 1.6 | 1.4 | 2.126 | 0.875
Interlaced Center Tapped Transformer Impedances
Rating | R0 | X0 | R1 | X1 | R2 | X2
kVA | % | % | % | % | % | %
100 CT | 0.5 | 1.68 | 1 | 0.84 | 1 | 0.84
50 CT | 0.55 | 1.44 | 1.1 | 0.72 | 1.1 | 0.72
All Distribution System Three-Phase Transformers
Rating | % Impedance
kVA | R | X | Z | X/R | Zgp(Ohms)
500 | 0.8 | 2.5 | 2.6249 | 3.125 | 25

## Loads
Distributed Loads
|  |  |  | Phase 1 |  | Phase 2 |  | Phase 3
Line | Node X | Node Y | Model | kW | kvar | kW | kvar | kW | kvar
OH-6 | 717 | 727 | Y-PQ | 50 | 15 | 35 | 10 | 10 | 5 | Total Per Phase
OH-7 | 727 | 731 | Y-Z | 25 | 12 | 15 | 5 | 30 | 20 | Ph A |  | Ph B |  | Ph C |  | Total
OH-11 | 742 | 744 | Y-PQ | 300 | 150 | 250 | 100 | 400 | 250 | kW | kVAR | kW | kVAR | kW | kVAR | kW | kVAR
OH-12 | 745 | 746 | Y-I | 10 | 7 | 10 | 7 | 10 | 7 | 1103.99 | 547.02 | 1225.47 | 481.06 | 1436.04 | 786.06 | 3765.5 | 1814.14
OH-13 | 746 | 747 | D-PQ | 35 | 15 | 25 | 12 | 20 | 8
OH-14 | 747 | 749 | D-Z |  |  |  |  | 50 | 25
OH-16 | 749 | 752 | D-I | 100 | 50 | 200 | 60 | 300 | 180
Non Center Tap Transformer Loads
|  |  |  | Phase 1 |  | Phase 2 |  | Phase 3
Xfm. No. | Ld. Node |  | Model | kW | kvar | kW | kvar | kW | kvar
T1 | 715 |  | Y-PQ | 80 | 30 | 80 | 30 | 80 | 30
T3 | 728 |  | D-I | 20 | 10 | 8 | 5 | 10 | 9
T5 | 740 |  | D-Z | 35 | 15 | 25 | 10 | 15 | 10
T7 | 743 |  | D-I | 80 | 40 | 80 | 40 | 80 | 40
T9 | 751 |  | Ind. Gen
T11 | 756 |  | Y-Z | 50 | 20 | 30 | 15 | 75 | 35
T12 | 759 |  | D-PQ |  |  | 35 | 20
T13 | 762 |  | Mtr. 2
T15 | 770 |  | D-PQ | 150 | 100 | 125 | 60 | 175 | 80
T16 | 708 |  | D-PQ | 75 | 40
T17 | 710 |  | Y-PQ |  |  | 80 | 30
T19 | 772 |  | Y-PQ |  |  | 50 | 25 | 50 | 25
T23 | 730 |  | D-PQ |  |  | 85 | 15
T24 | 714 |  | Mrt. 1
Center Tap Transformer Loads
|  |  |  | 120 V Ld-1 |  | 120 V Ld-2 |  | 240 V Ld-12
Xfm. No. | Ld. Node | Type | Model | kW | kvar | kW | kvar | kW | kvar
T2 | 620 | Lighting | CT-PQ | 1.57 | 0.51 | 2.36 | 0.77 | 3.92 | 1.9
| 621 | Lighting | CT-PQ | 2 | 0.66 | 3.01 | 0.99 | 5.01 | 2.43
| 622 | Lighting | CT-PQ | 2.54 | 0.83 | 1.69 | 0.56 | 4.23 | 1.05
| 623 | Lighting | CT-PQ | 0.79 | 0.26 | 1.18 | 0.39 | 1.97 | 0.95
| 624 | Lighting | CT-PQ | 3.64 | 1.12 | 5.46 | 1.79 | 9.1 | 4.41
| 625 | Lighting | CT-PQ | 2.16 | 0.71 | 1.44 | 0.47 | 3.6 | 1.47
| 626 | Lighting | CT-PQ | 2.09 | 0.68 | 3.03 | 1.03 | 5.21 | 2.52
T4 | 632 | Lighting | CT-PQ | 9.1 | 4.41 | 5.46 | 1.79 | 3.64 | 1.12
| 633 | Lighting | CT-PQ | 3.6 | 1.74 | 1.44 | 0.47 | 2.16 | 0.71
| 734 | Mtr. 4
T6 | 739 | Lighting | CT-PQ | 3.5 | 1.1 | 2.4 | 0.8 | 5.2 | 2.5
| 739 | 3-Ph | D-I | 10 | 5 | 10 | 5 | 10 | 5
T8 | 748 | Lighting | CT-Z | 8 | 4 | 10 | 5 | 15 | 10
| 748 | Mt. 3
T14 | 764 | Lighting | CT-Z | 8 | 4 | 5 | 3 | 12 | 9
|  | 3-Ph | D-Z | 7 | 3 | 7 | 3 | 7 | 3
T18 | 712 | Lighting | CT-DI | 20 | 10 | 15 | 6 | 30 | 10
T22 | 769 | Lighting | CT-DI | 5 | 3 | 8 | 0 | 10 | 5
|  | 3-Ph | D-I | 5 | 2 | 10 | 6 | 3 | 1
Y-PQ means a wye connected load modeled as constant kW and kvar
Y-I means a wye connected load modeled as a constant current and power factor computed at nominal voltage
Y-Z means a wye connected load modeled as a constant R + jX
D-PQ means a wye connected load modeled as constant kW and kvar
D-I means a wye connected load modeled as a constant current and power factor computed at nominal voltage
D-Z means a wye connected load modeled as a constant R + jX
CT-PQ means the two 120 V and 240 volt loads are modeled as constant kW and kvar
CT-I means the two 120 V and 240 volt loads are modeled as constant current and power factor computed at nominal voltage
CT-Z means the two 120 V and 240 volt loads are modeled as constant R +jX

## Switches
Switches
Switch Number | Node X | Node Y | Position
SW-1 | 741 | 745 | Closed
SW-2 | 744 | 757 | Open
SW-3 | 703 | 713 | Closed

## Machines
Machines
Machine ID | Node | Hp Rating | Rated Voltage | Stator R (PU) | Stator X (PU) | Rotor R (PU) | Rotor X (PU) | Mag. X (PU) | Operating Spec
Motor 1 | 716 | 25 | 480 | 0.0366 | 0.08 | 0.0394 | 0.08 | 2.1 | slip = 3.5
Motor 2 | 762 | 50 | 480 | 0.0699 | 0.1465 | 0.0425 | 0.1107 | 2.7127 | kW input = 45
Motor 3 | 748 | 50 | 240 | [5 empty] | HP = 45, PF = 85% Eff = 85%
Motor 4 | 734 | 25 | 240 | 0.0366 | 0.08 | 0.0394 | 0.08 | 2.1 | slip = 3.5
Ind Gen | 751 | 150 | 480 | 0.0651 | 0.1628 | 0.0553 | 0.1139 | 4.069 | kW out = 150

## Capacitors
Shunt Capacitors
|  |  | Phase a(ab) | Phase b(bc) | Phase c(ca)
Cap Number | Node | Connection | kvar | kvar | kvar | Switch
Cap 1 | 736 | Y | 100 | 100 | 100 | Closed
Cap 2 | 755 | Y | 50 | 50 | 50 | Closed
Cap 3 | 760 | Y | 100 | 100 | 100 | Closed
Cap 4 | 768 | D | 50 | 50 | 50 | Closed

## Regulators
Voltage Regulators
| 32 Step | Step Size | No. of Steps | Bandwidth
All Regulators | ±10 % | 5/8 % | 16 | 2
Regs with same settings
Reg. Number | Node X | Node Y | Connection | Regulator type | Phases | PT Rating | CT Rating | Set V Level | Set Comp R | Set Comp X | Mode
Reg 1 | 701 | 702 | Y-Y | 3 single phase | a-b-c | 120 | 200 | 123 | 4.7 | 3.4 | Infinite Tap
Reg 2 | 735 | 736 | Y-Y | 3 single phase | a-b-c | 120 | 100 | 124 | 3.6 | 2.8 | Infinite Tap
Reg 3 | 766 | 767 | D-D | 3 single phase | ab-bc-ca | 60 | 50 | 122 | 0 | 0 | Infinite Tap
Reg 4 | 717 | 718 | Wye | 1 single phase | a | 120 | 100 | 125 | 1.3 | 0.5 | Infinite Tap
Reg with diff. settings
Reg 5 | 705 | 706 | Open D-D | 2 singel phase | ab | 60 | 50 | 120 | 0 | 0.6 | Infinite Tap
[5 empty] | bc | 60 | 50 | 120 | 0.7 | 0.1 | Infinite Tap