## Part 1_Question 1
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 1: Design criteria, theory, and assumptions:
Are soil resistivity measurements made before designing the grounding system for: | Are soil resistivity measurements made before designing the grounding system for: | Are soil resistivity measurements made before designing the grounding system for: | Are soil resistivity measurements made before designing the grounding system for: | Are soil resistivity measurements made before designing the grounding system for:
Answer Options | Answer Options | Yes | No | Response Count
Generation Substation | Generation Substation | 52 | 3 | 55
Transmission Substation | Transmission Substation | 79 | 4 | 83
Distribution Substation | Distribution Substation | 67 | 9 | 76
Industrial Substation | Industrial Substation | 40 | 11 | 51
answered question | answered question | answered question | 87 | 87
skipped question | skipped question | skipped question | 18 | 18

## Part 1_Question 2
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 1: Design criteria, theory, and assumptions:
What is the basis for the safety criteria used in the design of your grounding system? | What is the basis for the safety criteria used in the design of your grounding system? | What is the basis for the safety criteria used in the design of your grounding system? | What is the basis for the safety criteria used in the design of your grounding system? | What is the basis for the safety criteria used in the design of your grounding system? | What is the basis for the safety criteria used in the design of your grounding system?
Answer Options | Answer Options | IEEE Std 80 | IEC Design Criteria | Other, list below | Response Count
Generation | Generation | 51 | 1 | 8 | 56
Transmission | Transmission | 75 | 6 | 15 | 83
Distribution | Distribution | 69 | 2 | 16 | 76
Industrial | Industrial | 44 | 1 | 10 | 50
Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | 22 | 22
answered question | answered question | answered question | answered question | 86 | 86
skipped question | skipped question | skipped question | skipped question | 19 | 19
Number | Response Date | Other (please specify)
1 | 2009-06-08 22:09 | Entergy Standards
2 | 2009-06-08 23:02 | IEEE837 transformer neutral connections and electrode connections. AS3835 Earth potential rise protection of telecommunication network users. AS 60479 effects of current on human beings and livestock as2067 Substation and high voltage installation exceeding 1kV ac ENA EG1 2006 substation earthing guide IEEE 80& 81 Several Design Standards people are still of the belief that more copper is good enough, unfortunately. Also the type and use of connection methods swings heavily towards time and expense factors rather than safety criteria being met - especially under fault conditions.
3 | 2009-06-09 04:52 | IEEE 142 NFPA70 (NEC)
4 | 2009-06-09 14:40 | ONTARIO HYDRO TRANSMISSION AND DISTRIBUTION GUIDE BOOK-1994 Edition
5 | 2009-06-10 08:09 | Australian Standards
6 | 2009-06-10 16:06 | IEEE stds 837, 487, 142, 81, 81.2
7 | 2009-06-10 16:20 | IEEE stds 837, 487, 142, 81, 81.2
8 | 2009-06-11 08:22 | Japanese low
9 | 2009-06-12 10:09 | IEC 61936-1, THE CORRESPONDING EURONORM AND ITS FINNISH TRANSLATION SFS 6001 WITH SPECIAL EXCEPTIONS
10 | 2009-06-15 05:41 | ENA Substation Earthing Guide
11 | 2009-06-19 13:27 | Parametric Studies
12 | 2009-06-23 08:35 | ENA EG1: 2006 :SUBSTATION EARTHING GUIDE AS 2067—2008: Substations and high voltage installations exceeding 1 kV a.c. ENA C(b)1—2006: GUIDELINES FOR DESIGN AND MAINTENANCE OF OVERHEAD DISTRIBUTION AND TRANSMISSION LINES AS/NZS 4853:2000: Electrical hazards on metallic pipelines
13 | 2009-06-29 15:55 | NESC
14 | 2009-06-30 00:21 | ENA-EG1 2006 Substation Earthing Guide (equivelant to Australian standard developed with our envolvement)
15 | 2009-06-30 05:23 | Company Policy & guidelines
16 | 2009-06-30 14:35 | Cell sites on transmission towers
17 | 2009-07-01 01:51 | ENA EG1 - 2006 Substation Earthing Guide
18 | 2009-07-08 23:41 | ESAA EG1:Substation Earthing Code.
19 | 2009-07-09 21:18 | IEEE 80 and ENA (Electricity Networks Aust) EG1. For the industrial (consumer) applications a number of pre-defined arrangements are used based on EG1, and AS3000.
20 | 2009-07-14 14:50 | Ontario Hydro Transmission and Distribution Grounding Guide 1994 Edition
21 | 2009-07-21 01:52 | We use a program based upon IEEE 80
22 | 2009-08-31 00:33 | DL/T 621-1997

## Part 1_Question 3
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 1: Design criteria, theory, and assumptions:
Which computer program do you use to analyze the grounding system? | Which computer program do you use to analyze the grounding system? | Which computer program do you use to analyze the grounding system? | Which computer program do you use to analyze the grounding system? | Which computer program do you use to analyze the grounding system? | Which computer program do you use to analyze the grounding system? | Which computer program do you use to analyze the grounding system? | Which computer program do you use to analyze the grounding system? | Which computer program do you use to analyze the grounding system? | Which computer program do you use to analyze the grounding system? | Which computer program do you use to analyze the grounding system? | Which computer program do you use to analyze the grounding system?
Answer Options | Answer Options | CDEGS | WINIGS | EPRI SGW | EPRI SDW | ETAP | SKM | CYME | None | Other, list below | Response Count
Generation | Generation | 25 | 17 | 2 | 0 | 1 | 0 | 0 | 0 | 6 | 49
Transmission | Transmission | 41 | 23 | 2 | 0 | 1 | 0 | 2 | 2 | 9 | 75
Distribution | Distribution | 32 | 23 | 2 | 0 | 1 | 0 | 0 | 5 | 6 | 67
Industrial | Industrial | 18 | 17 | 1 | 0 | 2 | 1 | 0 | 3 | 3 | 42
Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | 17 | 17
answered question | answered question | answered question | answered question | answered question | answered question | answered question | answered question | answered question | answered question | 79 | 79
skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | 26 | 26
Number | Response Date | Other (please specify)
1 | 2009-06-08 22:09 | Excel Spreadsheet
2 | 2009-06-08 23:02 | Please see Glen barnes and Luke Clout for specific programs
3 | 2009-06-09 00:55 | 1. In-house program (based on IEEE STD 80) 2. SES (Safe Engineering Services) software 3. Consultants (Their own Software)
4 | 2009-06-09 12:35 | Excel program
5 | 2009-06-09 16:45 | Computer program used for generation projects depends on consultant engineer hired for the specific project.
6 | 2009-06-10 08:51 | We use CDEGS MALT for small substations and MALZ for large transmission substations.
7 | 2009-06-10 11:51 | We use an internally developed Excel spreadsheet
8 | 2009-06-11 08:22 | COULOMB
9 | 2009-06-12 10:09 | When needed, own programmes. because the substations are constructed as turn-key deliveries, a big part of the design tasks belong to the contractors.
10 | 2009-06-15 05:41 | Our earthing consultants use CDEGS.
11 | 2009-06-17 15:52 | dont know
12 | 2009-06-23 08:35 | PSIM, AVC, WinRes
13 | 2009-06-29 21:42 | Spreadsheet based on IEEE 80 formulas
14 | 2009-06-30 13:16 | Excel spread sheet using IEEE 80 formula
15 | 2009-06-30 14:35 | Cell sites on transmission towers
16 | 2009-07-02 20:39 | SafeEarth (Australia) is also permitted for use by our design service providers.
17 | 2009-08-31 00:33 | MathCAD

## Part 1_Question 4
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 1: Design criteria, theory, and assumptions:
What is the basic design criteria used in the soil structure calculations? | What is the basic design criteria used in the soil structure calculations? | What is the basic design criteria used in the soil structure calculations? | What is the basic design criteria used in the soil structure calculations?
Answer Options | Answer Options | Response Percent | Response Count
Equivalent uniform soil resistivity | Equivalent uniform soil resistivity | 24.7% | 20
Two layer soil resistivity | Two layer soil resistivity | 53.1% | 43
Multi layer soil resistivity | Multi layer soil resistivity | 38.3% | 31
Other, list below | Other, list below | 4.9% | 4
Other (please specify) | Other (please specify) | 8 | 8
answered question | answered question | 81 | 81
skipped question | skipped question | 24 | 24
Number | Response Date | Other (please specify)
1 | 2009-06-08 23:02 | Due to the quite fluctuating structure of soils within the wide geographic nature of NSW a multi layer model is required
2 | 2009-06-10 08:51 | We typically use two layer or multi layer and check if there is a major difference between the two.
3 | 2009-06-12 10:09 | The adequacy of design calculations is checked with measurements when the substation is ready. Additional earthing electrodes are drawn along the right-of-way when necessary
4 | 2009-06-15 05:06 | Occasionally also use uniform or continuous type layers.
5 | 2009-06-23 08:35 | For LFI studies Equivalent Soil For EPR studies mainly two layer
6 | 2009-06-30 00:21 | Finite element method
7 | 2009-06-30 14:35 | We let the program decide the best soil structure. Occassionally, vertical or hemispherical soil models are need to get FOP matching.
8 | 2009-08-10 19:42 | Typically I try to keep to two soil layers, unless the soil warrants more than two. CDEGS on its own will tend to go to three layers with little difference between two of the layers, in which case I force it to two layers. With the winter case that the client usually requests, a third top layer is added with high resistivity.

## Part 1_Question 5
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 1: Design criteria, theory, and assumptions:
What is the basic design criteria used to calculate the configuration of the grounding electrode? | What is the basic design criteria used to calculate the configuration of the grounding electrode? | What is the basic design criteria used to calculate the configuration of the grounding electrode? | What is the basic design criteria used to calculate the configuration of the grounding electrode?
Answer Options | Answer Options | Response Percent | Response Count
Grid conductors equally spaced with ground rods. | Grid conductors equally spaced with ground rods. | 48.8% | 39
Grid conductors equally spaced without ground rods. | Grid conductors equally spaced without ground rods. | 8.8% | 7
Grid conductors not equally spaced with ground rods. | Grid conductors not equally spaced with ground rods. | 37.5% | 30
Grid conductors not equally spaced without ground rods. | Grid conductors not equally spaced without ground rods. | 6.3% | 5
Grid conductors designed around civil structures and equipment to control touch potential within reach of that structure or equipment. | Grid conductors designed around civil structures and equipment to control touch potential within reach of that structure or equipment. | 57.5% | 46
Other (please specify) | Other (please specify) | 9 | 9
answered question | answered question | 80 | 80
skipped question | skipped question | 25 | 25
Number | Response Date | Other (please specify)
1 | 2009-06-08 23:02 | CE due to the work load use several Electrical Design Consultants to carry out designs. G BArnes and L Clout give specific brief to these. There is a widely held belief taht every piece of metal - no matter how large or small is required to be earthed and therefore many grid size conductors are run independently of the main grid. this practice is being reduced as education increases.
2 | 2009-06-09 17:37 | More concentration of grid at corners of station.
3 | 2009-06-09 17:45 | closer spacing at grid corners
4 | 2009-06-10 08:51 | Use of vertical groung rods will depend on the resistivity of the deeper layers of soil. If it is low resistivity, and first pass design results are not good, we will investigate the use of ground rods.
5 | 2009-06-15 05:06 | We use all configurations depending on the site conditions, eg Green/brown field, effectiveness of existing grids etc.
6 | 2009-06-18 12:04 | Grid conductors are generally equal spaced, but overlayed on foundation plan to ensure conductors do not go through foundations and to make sure enough grid conductors are available to connect equipment and structure risers to nearby grid.
7 | 2009-07-02 20:39 | Ground rods are rarely used.
8 | 2009-07-09 21:18 | The design also includes grading rings etc around structures and non-current carrying metalwork.
9 | 2009-08-10 19:42 | The grid conductors are mostly evenly spaced, but a smaller spacing is usually used for the last "block" around the perimeter.

## Part 1_Question 6
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 1: Design criteria, theory, and assumptions:
How do you generally determine the maximum grid current for your design? | How do you generally determine the maximum grid current for your design? | How do you generally determine the maximum grid current for your design? | How do you generally determine the maximum grid current for your design?
Answer Options | Answer Options | Response Percent | Response Count
The maximum available short circuit current at the buss. | The maximum available short circuit current at the buss. | 51.9% | 41
The fault current rating of the equipment. | The fault current rating of the equipment. | 8.9% | 7
Determine the actual grid current considering the effects of alternating ground paths (current splits). | Determine the actual grid current considering the effects of alternating ground paths (current splits). | 58.2% | 46
Other (please specify) | Other (please specify) | 9 | 9
answered question | answered question | 79 | 79
skipped question | skipped question | 26 | 26
Number | Response Date | Other (please specify)
1 | 2009-06-08 23:02 | There are several factors taken into account which are different for green field sites vs brown field sites. If it as an addition of equipment which will not raise fault level then usually an extension of the grid is based on existing conductor size. Increase in fault level determines remodelling fault currents and if required - ie North Coffs Harbour. Whole earthgrid conductor size increased to new conductor size where appropriate.
2 | 2009-06-09 04:52 | Single Line to Ground Fault Current
3 | 2009-06-09 12:32 | add 25% growth factor to P&C provided value forcasted 10 years in future.
4 | 2009-06-10 08:51 | If the maximum buss current is proving difficult to design for, we will than determine the actual grid current considering the effects of alternating ground paths. We take the actual maximum zero sequence fault current over the lifespan of the station. It is sometimes very difficult and costly to design for current rating of equipment when the actual fault current is much lower than the equipment rating.
5 | 2009-06-15 05:06 | We begin the first pass of our designs using maximum short circuit currents as determined by our Network Planning branch. If the proposed grid is inadequate for that current level we will consider other factors, the first of which is usually by determining a current split.
6 | 2009-06-18 12:04 | Use system base case case for 5 years into future, plus bump everything up 10% for additional future growth.
7 | 2009-06-30 13:16 | Maximum available short circuit current with allowance for growth.
8 | 2009-07-09 21:18 | Including future (ultimate) fault levels.
9 | 2009-08-10 19:42 | Again, client needs usually dictate the current split calculations that are allowed. Without client standards, we run current splits with ultimate configurations considered.

## Part 1_Question 7
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 1: Design criteria, theory, and assumptions:
Do you model other details of the system nearby structures (lines, buried pipes, touch voltage on water tap, etc, etc,,,)? | Do you model other details of the system nearby structures (lines, buried pipes, touch voltage on water tap, etc, etc,,,)? | Do you model other details of the system nearby structures (lines, buried pipes, touch voltage on water tap, etc, etc,,,)? | Do you model other details of the system nearby structures (lines, buried pipes, touch voltage on water tap, etc, etc,,,)?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 45.7% | 37
No | No | 54.3% | 44
answered question | answered question | 81 | 81
skipped question | skipped question | 24 | 24

## Part 1_Question 8
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 1: Design criteria, theory, and assumptions:
In determining the value of fault current flowing into the grid, do you assume a single phase to ground fault on the system? | In determining the value of fault current flowing into the grid, do you assume a single phase to ground fault on the system? | In determining the value of fault current flowing into the grid, do you assume a single phase to ground fault on the system? | In determining the value of fault current flowing into the grid, do you assume a single phase to ground fault on the system?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 88.6% | 70
No | No | 11.4% | 9
answered question | answered question | 79 | 79
skipped question | skipped question | 26 | 26

## Part 1_Question 9
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 1: Design criteria, theory, and assumptions:
In determining the value of fault current flowing into the grid, do you assume the grid resistance is in series with the zero sequence impedance of the system? | In determining the value of fault current flowing into the grid, do you assume the grid resistance is in series with the zero sequence impedance of the system? | In determining the value of fault current flowing into the grid, do you assume the grid resistance is in series with the zero sequence impedance of the system? | In determining the value of fault current flowing into the grid, do you assume the grid resistance is in series with the zero sequence impedance of the system?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 72.2% | 52
No | No | 27.8% | 20
answered question | answered question | 72 | 72
skipped question | skipped question | 33 | 33

## Part 1_Question 10
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 1: Design criteria, theory, and assumptions:
In determining the value of fault current flowing into the grid, do you assume the fault current divides between the various metallic paths (for example distribution neutrals, shields, pipes, etc,,,,) and the ground grid? Please specify the method of calculation: | In determining the value of fault current flowing into the grid, do you assume the fault current divides between the various metallic paths (for example distribution neutrals, shields, pipes, etc,,,,) and the ground grid? Please specify the method of calculation: | In determining the value of fault current flowing into the grid, do you assume the fault current divides between the various metallic paths (for example distribution neutrals, shields, pipes, etc,,,,) and the ground grid? Please specify the method of calculation: | In determining the value of fault current flowing into the grid, do you assume the fault current divides between the various metallic paths (for example distribution neutrals, shields, pipes, etc,,,,) and the ground grid? Please specify the method of calculation:
Answer Options | Answer Options | Response Percent | Response Count
Curves in IEEE Std 80-2000 | Curves in IEEE Std 80-2000 | 35.8% | 24
Software program that models the power system as well as alternate paths | Software program that models the power system as well as alternate paths | 70.1% | 47
Formulas that compute the equivalent impedance of each alternate ground path | Formulas that compute the equivalent impedance of each alternate ground path | 13.4% | 9
Other (please specify) | Other (please specify) | 11 | 11
answered question | answered question | 67 | 67
skipped question | skipped question | 38 | 38
Number | Response Date | Other (please specify)
1 | 2009-06-08 23:02 | ( and 10 should be determined on appropriate substation and is a question for Glen Barnes, Luke Clout. There is differing opinion from others in CE however These two gentlemens opinion is the most educated in this area.
2 | 2009-06-09 11:33 | We use a data table created by our system protection engineers.
3 | 2009-06-09 12:35 | Purposely allow "extra" ground grid (since there with manpower and equipment installing anyway) and do not depend upon external metallic paths.
4 | 2009-06-12 10:09 | The reduction factor determined by earthwires and, cable shields etc is taken into account, the other metallic pipe works not because we cannot be sure about their condition.
5 | 2009-06-15 17:37 | 8. Also consider 2L-G fault 9. Normally ignore it. 10. Non-continuous shield wire, so no current split.
6 | 2009-06-16 20:05 | Since we do not model the entire system, we use the maximum single phase to ground fault current and use a split factor of 1.0.
7 | 2009-06-29 18:17 | We neglect the current division. We design for 100% fault current level.
8 | 2009-06-30 13:16 | Assume all current flows into ground grid
9 | 2009-06-30 14:35 | Model the various paths in CDEGS till FOP matching is achieved
10 | 2009-07-09 21:18 | As a conservative approach, we assume the full fault current flows into the grid. This approach is taken, as we only perform Soil Resistivity test once (at the start of the design) and the ground conditions can change over the life of the installation, and the fault level can change in the grid - depending on network switching configurations.
11 | 2009-07-14 14:50 | Q#8: We are considering biggest value of L-G or LL-G fault

## Part 2_Question 1
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
Do you calculate the grounding grid resistance for substations? | Do you calculate the grounding grid resistance for substations? | Do you calculate the grounding grid resistance for substations? | Do you calculate the grounding grid resistance for substations? | Do you calculate the grounding grid resistance for substations?
Answer Options | Answer Options | Yes | No | Response Count
Generation | Generation | 46 | 3 | 49
Transmission | Transmission | 70 | 1 | 71
Distribution | Distribution | 59 | 4 | 63
Industrial | Industrial | 34 | 6 | 40
answered question | answered question | answered question | 74 | 74
skipped question | skipped question | skipped question | 31 | 31

## Part 2_Question 2
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
Do you calculate the ground grid potential rise for substations? | Do you calculate the ground grid potential rise for substations? | Do you calculate the ground grid potential rise for substations? | Do you calculate the ground grid potential rise for substations? | Do you calculate the ground grid potential rise for substations?
Answer Options | Answer Options | Yes | No | Response Count
Generation | Generation | 47 | 2 | 49
Transmission | Transmission | 71 | 0 | 71
Distribution | Distribution | 59 | 3 | 62
Industrial | Industrial | 34 | 5 | 39
answered question | answered question | answered question | 74 | 74
skipped question | skipped question | skipped question | 31 | 31

## Part 2_Question 3
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
Do you have a maximum allowable ground potential rise? | Do you have a maximum allowable ground potential rise? | Do you have a maximum allowable ground potential rise? | Do you have a maximum allowable ground potential rise?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 34.7% | 25
No | No | 65.3% | 47
answered question | answered question | 72 | 72
skipped question | skipped question | 33 | 33

## Part 2_Question 4
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
If "YES" to question 3, what is the maximum permitted ground grid potential rise for substations? | If "YES" to question 3, what is the maximum permitted ground grid potential rise for substations? | If "YES" to question 3, what is the maximum permitted ground grid potential rise for substations? | If "YES" to question 3, what is the maximum permitted ground grid potential rise for substations? | If "YES" to question 3, what is the maximum permitted ground grid potential rise for substations? | If "YES" to question 3, what is the maximum permitted ground grid potential rise for substations? | If "YES" to question 3, what is the maximum permitted ground grid potential rise for substations? | If "YES" to question 3, what is the maximum permitted ground grid potential rise for substations?
Answer Options | Answer Options | < 1kV | 1 - 5 kV | 6 - 10 kV | 11 - 15 kV | > 16 kV | Response Count
Generation | Generation | 6 | 8 | 2 | 0 | 0 | 16
Transmission | Transmission | 7 | 11 | 5 | 0 | 1 | 24
Distribution | Distribution | 6 | 13 | 2 | 0 | 1 | 22
Industrial | Industrial | 5 | 5 | 1 | 0 | 0 | 11
answered question | answered question | answered question | answered question | answered question | answered question | 25 | 25
skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | 80 | 80

## Part 2_Question 5
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
If "YES" to question 3, what is the basic reason for this maximum potential rise? | If "YES" to question 3, what is the basic reason for this maximum potential rise? | If "YES" to question 3, what is the basic reason for this maximum potential rise? | If "YES" to question 3, what is the basic reason for this maximum potential rise?
Answer Options | Answer Options | Response Percent | Response Count
Insulation coordination for communication circuits? | Insulation coordination for communication circuits? | 80% | 20
Other, please specify | Other, please specify | 20% | 5
Other (please specify) | Other (please specify) | 7 | 7
answered question | answered question | 25 | 25
skipped question | skipped question | 80 | 80
Number | Response Date | Other (please specify)
1 | 2009-06-09 01:13 | calculated as based on Std 80 (old version, 1982)
2 | 2009-06-09 12:38 | More concerned with calculated ohmic value of ground grid.
3 | 2009-06-10 08:59 | Most comms equipment. modems etc are rated up to 5kV.
4 | 2009-06-11 04:49 | safety
5 | 2009-06-23 08:45 | Standards requirement
6 | 2009-06-29 17:28 | Ability to clear fault Control and signal wires Equipment rating (neutral bushing & neutral reators) Limit transfer of potential to perimeter fence
7 | 2009-06-29 23:05 | Allowable potential rise depends on the nature of the locality. Even at the transmission level the allowable potential rise is limited to 1kV. The reason being safety to public and personnel working for other utilities.

## Part 2_Question 6
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
Do you calculate Step Potentials? | Do you calculate Step Potentials? | Do you calculate Step Potentials? | Do you calculate Step Potentials? | Do you calculate Step Potentials?
Answer Options | Answer Options | Yes | No | Response Count
Within the Ground Grid | Within the Ground Grid | 68 | 1 | 69
Beyond the Ground Grid | Beyond the Ground Grid | 45 | 17 | 62
answered question | answered question | answered question | 71 | 71
skipped question | skipped question | skipped question | 34 | 34

## Part 2_Question 7
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
If "YES" to "Beyond the Ground Grid" in question 6, how far beyond? | If "YES" to "Beyond the Ground Grid" in question 6, how far beyond? | If "YES" to "Beyond the Ground Grid" in question 6, how far beyond? | If "YES" to "Beyond the Ground Grid" in question 6, how far beyond? | If "YES" to "Beyond the Ground Grid" in question 6, how far beyond? | If "YES" to "Beyond the Ground Grid" in question 6, how far beyond? | If "YES" to "Beyond the Ground Grid" in question 6, how far beyond? | If "YES" to "Beyond the Ground Grid" in question 6, how far beyond? | If "YES" to "Beyond the Ground Grid" in question 6, how far beyond?
Feet | Feet | Feet | Feet | Feet | Feet | Feet | Feet | Feet
Answer Options | Answer Options | 3 | 6 | 9 | 12 | 15 | 18 | Response Count
Distance | Distance | 11 | 7 | 3 | 2 | 0 | 4 | 27
Meters | Meters | Meters | Meters | Meters | Meters | Meters | Meters
Answer Options | Answer Options | 1 | 2 | 3 | 4 | 5 | Response Count
Distance | Distance | 2 | 3 | 2 | 0 | 4 | 11
[7 empty] | Question Totals | Question Totals
Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | 15 | 15
answered question | answered question | answered question | answered question | answered question | answered question | answered question | 38 | 38
skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | 67 | 67
Number | Response Date | Other (please specify)
1 | 2009-06-09 04:57 | 3 feet beyond the substation fence
2 | 2009-06-09 12:48 | Until the safe limit is reached.
3 | 2009-06-09 13:12 | 3-5 ft grid extended beyond fence.
4 | 2009-06-10 08:20 | As fas as required
5 | 2009-06-10 08:59 | We calculate step and touch potentials for people within reach of the fence from outside the substation, typically 1m. Step potentials are usually not a problem. We use yardstone 1.2m outside the fence as well as the entire yard inside.
6 | 2009-06-12 10:53 | The step potentials are avoided by usinf of buried auxiliary earthing electrodes near metallic or conductive structures which can be touched
7 | 2009-06-15 05:14 | In some circumstances (eg metropolitan area) we will examine EPR/step voltages for considerable distances beyond the ground grid.
8 | 2009-06-15 22:45 | As far as necessary in order to maintain safety limits
9 | 2009-06-19 13:31 | As far as the hazard extends (i.e. when the relevant limit is no longer exceeded)
10 | 2009-06-29 18:14 | About 10 feet from the station fence.
11 | 2009-06-29 23:05 | Till the potential comes to acceptable levels.
12 | 2009-06-30 00:27 | also include step voltages in the areas associated with other metallic facilities
13 | 2009-07-02 20:54 | No specific distance. Consideration is given to any location adjacent to the substation where excessive step potentials are shown to occur.
14 | 2009-07-09 21:24 | No defined distance. We just confirm that there are no 'step potential' issues outside and inside of the substation fence.
15 | 2009-07-14 14:57 | 1.5 meter beyound station fence

## Part 2_Question 8
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
Do you calculate Touch (mesh) Potentials? | Do you calculate Touch (mesh) Potentials? | Do you calculate Touch (mesh) Potentials? | Do you calculate Touch (mesh) Potentials? | Do you calculate Touch (mesh) Potentials?
Answer Options | Answer Options | Yes | No | Response Count
Within the Ground Grid | Within the Ground Grid | 69 | 1 | 70
Beyond the Ground grid | Beyond the Ground grid | 39 | 17 | 56
answered question | answered question | answered question | 72 | 72
skipped question | skipped question | skipped question | 33 | 33

## Part 2_Question 9
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
As a design criteria, are you using primary or back-up clearing times? | As a design criteria, are you using primary or back-up clearing times? | As a design criteria, are you using primary or back-up clearing times? | As a design criteria, are you using primary or back-up clearing times?
Answer Options | Answer Options | Response Percent | Response Count
Primary | Primary | 30% | 21
Back-up | Back-up | 70% | 49
answered question | answered question | 70 | 70
skipped question | skipped question | 35 | 35

## Part 2_Question 10
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
Do you use Actual or Assumed clearing time values? | Do you use Actual or Assumed clearing time values? | Do you use Actual or Assumed clearing time values? | Do you use Actual or Assumed clearing time values?
Answer Options | Answer Options | Response Percent | Response Count
Actual | Actual | 27.8% | 20
Assumed | Assumed | 72.2% | 52
answered question | answered question | 72 | 72
skipped question | skipped question | 33 | 33

## Part 2_Question 11
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
What clearing time values do yo use? | What clearing time values do yo use? | What clearing time values do yo use? | What clearing time values do yo use? | What clearing time values do yo use? | What clearing time values do yo use? | What clearing time values do yo use? | What clearing time values do yo use? | What clearing time values do yo use?
Answer Options | Answer Options | 0 - 10 Cycles | 11 - 20 Cycles | 21 - 30 Cycles | 31 - 60 Cycles | 61 - 180 Cycles | > 181 Cycles | Response Count
Generation | Generation | 16 | 8 | 13 | 2 | 1 | 0 | 40
Transmission | Transmission | 18 | 12 | 32 | 1 | 1 | 0 | 64
Distribution | Distribution | 3 | 9 | 24 | 11 | 10 | 0 | 57
Industrial | Industrial | 2 | 11 | 11 | 3 | 5 | 0 | 32
answered question | answered question | answered question | answered question | answered question | answered question | answered question | 66 | 66
skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | 39 | 39

## Part 2_Question 12
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
Are the touch and step potential values derived from Dalziel's formula where I (Amperes) = K/√t, where K is the constant related to the weight of the person, and t is the clearing time in seconds? | Are the touch and step potential values derived from Dalziel's formula where I (Amperes) = K/√t, where K is the constant related to the weight of the person, and t is the clearing time in seconds? | Are the touch and step potential values derived from Dalziel's formula where I (Amperes) = K/√t, where K is the constant related to the weight of the person, and t is the clearing time in seconds? | Are the touch and step potential values derived from Dalziel's formula where I (Amperes) = K/√t, where K is the constant related to the weight of the person, and t is the clearing time in seconds?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 86.6% | 58
No | No | 13.4% | 9
answered question | answered question | 67 | 67
skipped question | skipped question | 38 | 38

## Part 2_Question 13
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
If "YES" to the prior question, which K constant value is used? | If "YES" to the prior question, which K constant value is used? | If "YES" to the prior question, which K constant value is used? | If "YES" to the prior question, which K constant value is used?
Answer Options | Answer Options | Response Percent | Response Count
K = (70 kg) | K = (70 kg) | 19.7% | 12
K = (50 kg) | K = (50 kg) | 67.2% | 41
K = Other, please specify below | K = Other, please specify below | 13.1% | 8
Other (please specify) | Other (please specify) | 10 | 10
answered question | answered question | 61 | 61
skipped question | skipped question | 44 | 44
Number | Response Date | Other (please specify)
1 | 2009-06-10 08:20 | K = (70 kg) and (50 kg) have been used, depending on the situation
2 | 2009-06-12 10:53 | IEC's curve for the touch potentials
3 | 2009-06-14 22:19 | 70kg within fenced enclosure, 50kg outside fence
4 | 2009-06-15 05:14 | Both: 70kg inside substations and 50kg outside.
5 | 2009-06-15 05:47 | Both is calculated
6 | 2009-06-23 08:45 | Both 70kg for intermal and 50kg for external
7 | 2009-06-30 00:27 | Depending on inside or outside the site, different values been used. And furthermore, body resistance is to be adjusted (two feet standing on ground) for step voltage calculations
8 | 2009-07-01 02:02 | 50kg used for outside the fence
9 | 2009-07-02 20:54 | 70 kg within switchyard; 50 kg in public areas
10 | 2009-08-10 19:46 | Typically 70 kg, but 50 kg in some applications.

## Part 2_Question 14
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
Do you use surface material to decrease the possible body current under fault conditions? | Do you use surface material to decrease the possible body current under fault conditions? | Do you use surface material to decrease the possible body current under fault conditions? | Do you use surface material to decrease the possible body current under fault conditions?
Answer Options | Answer Options | Response Percent | Response Count
Always | Always | 63.9% | 46
Never | Never | 4.2% | 3
According to Company's standards, or to meet tolerable touch and step potentials. | According to Company's standards, or to meet tolerable touch and step potentials. | 31.9% | 23
answered question | answered question | 72 | 72
skipped question | skipped question | 33 | 33

## Part 2_Question 15
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
What type of surface material do you use? | What type of surface material do you use? | What type of surface material do you use? | What type of surface material do you use?
Answer Options | Answer Options | Response Percent | Response Count
Crushed Rock | Crushed Rock | 93% | 66
Asphalt | Asphalt | 31% | 22
Concrete | Concrete | 4.2% | 3
Shells | Shells | 0% | 0
Other, please specify | Other, please specify | 4.2% | 3
Other (please specify) | Other (please specify) | 10 | 10
answered question | answered question | 71 | 71
skipped question | skipped question | 34 | 34
Number | Response Date | Other (please specify)
1 | 2009-06-09 01:13 | Type II
2 | 2009-06-09 13:12 | 1300 ohms granite crusher run 8000 ohms #57 washed granite stone
3 | 2009-06-09 16:53 | Rounded stone, minimum 1" dia.
4 | 2009-06-09 20:19 | Special high resistivity rock, above 3000 ohm meter
5 | 2009-06-10 08:59 | crushed stone with minimum resistivity 3000 ohm-m when wet
6 | 2009-06-11 16:19 | ABC
7 | 2009-06-15 05:14 | We attempt to avoid the use of surface treatments. However, Q16, we do use them in some cases where touch/step voltages can't otherwise be controlled. Rock preferred and Asphalt (Bitumen) second choice due cost.
8 | 2009-06-30 14:39 | Only use asphalt when normal copper grounding solutions are not possible or economically practical
9 | 2009-07-02 20:54 | Crushed rock is preferred due to lower cost.
10 | 2009-07-09 21:24 | Crushed Rock inside the fence, and; asphalt on driveways and outside of the fence.

## Part 2_Question 16
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
Do you consider the surface materials in your calculations of tolerable step and touch potentials? | Do you consider the surface materials in your calculations of tolerable step and touch potentials? | Do you consider the surface materials in your calculations of tolerable step and touch potentials? | Do you consider the surface materials in your calculations of tolerable step and touch potentials?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 84.3% | 59
No | No | 15.7% | 11
answered question | answered question | 70 | 70
skipped question | skipped question | 35 | 35

## Part 2_Question 17
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
Do you measure the resistivity value of the surface materials, when they are wet? | Do you measure the resistivity value of the surface materials, when they are wet? | Do you measure the resistivity value of the surface materials, when they are wet? | Do you measure the resistivity value of the surface materials, when they are wet?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 28.6% | 20
No | No | 71.4% | 50
answered question | answered question | 70 | 70
skipped question | skipped question | 35 | 35

## Part 2_Question 18
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
If "YES" to the prior question, how do you measure the resistivity of the wet surface material? | If "YES" to the prior question, how do you measure the resistivity of the wet surface material? | If "YES" to the prior question, how do you measure the resistivity of the wet surface material?
Answer Options | Answer Options | Response Count
17
answered question | 17 | 17
skipped question | 88 | 88
Number | Response Date | Response Text
1 | 2009-06-09 00:16 | not in "Lab" conditions;same test values vary greatly
2 | 2009-06-09 01:13 | ANSI/IEEE Std 80-1986 Sec 10.5, Table 3, pg.73
3 | 2009-06-09 12:37 | By means of testing
4 | 2009-06-09 15:00 | For Crush stone, we collect a buckle of it and wet it with distilled water and measure resistivity of that
5 | 2009-06-09 16:53 | In a test jig made from 12" dia. PVC pipe.
6 | 2009-06-10 08:59 | This was done in a civil eng lab
7 | 2009-06-15 17:44 | BPA Test Procedure
8 | 2009-06-15 22:45 | Using a fixed volume container, filling it with wet/drained crushed rock then using a SYSCAL to inject current through the rock via injection plates, then measuring the voltage at the injection plates. This results in a resistance that can be converted to a resistivity using the appropriate equation
9 | 2009-06-18 12:11 | procedure involving a plastic bucket with holes for drainage and conductive mesh in bottom and on top of rock sample
10 | 2009-06-22 15:09 | periodic resistivity testing by lab
11 | 2009-06-23 08:45 | by measurement in the wet season or derating 20%
12 | 2009-06-29 18:14 | The tests were conducted by the former Ontario Hydro Research Division.
13 | 2009-06-30 00:27 | on site measurement the crushed rock with no fine and washed
14 | 2009-07-08 23:47 | Test rig within company
15 | 2009-07-14 14:57 | wet condition with dionized water
16 | 2009-07-21 13:33 | Simulated
17 | 2009-08-10 19:46 | Occasionally the client sends tested values for surface materials.

## Part 2_Question 19
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
Do you specify the surface material based upon wet measured resistivity values? | Do you specify the surface material based upon wet measured resistivity values? | Do you specify the surface material based upon wet measured resistivity values? | Do you specify the surface material based upon wet measured resistivity values?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 51.4% | 36
No | No | 48.6% | 34
answered question | answered question | 70 | 70
skipped question | skipped question | 35 | 35

## Part 2_Question 20
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
What range of wet "Crushed Rock" resistivity values do you use? | What range of wet "Crushed Rock" resistivity values do you use? | What range of wet "Crushed Rock" resistivity values do you use? | What range of wet "Crushed Rock" resistivity values do you use?
Answer Options | Answer Options | Response Percent | Response Count
< 1,000 Ω-M | < 1,000 Ω-M | 5% | 3
1,000 Ω-M to 2,999 Ω-M | 1,000 Ω-M to 2,999 Ω-M | 38.3% | 23
3,000 Ω-M to 5,999 Ω-M | 3,000 Ω-M to 5,999 Ω-M | 41.7% | 25
6,000 Ω-M to 9,999 Ω-M | 6,000 Ω-M to 9,999 Ω-M | 6.7% | 4
> 10,000 Ω-M | > 10,000 Ω-M | 5% | 3
Other, please specify | Other, please specify | 3.3% | 2
Other (please specify) | Other (please specify) | 2 | 2
answered question | answered question | 60 | 60
skipped question | skipped question | 45 | 45
Number | Response Date | Other (please specify)
1 | 2009-06-15 17:44 | Min 3000, no maximum
2 | 2009-06-15 22:45 | minimum of 3000 ohm-m

## Part 2_Question 21
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
What range of wet "Concrete" resistivity values do you use? | What range of wet "Concrete" resistivity values do you use? | What range of wet "Concrete" resistivity values do you use? | What range of wet "Concrete" resistivity values do you use?
Answer Options | Answer Options | Response Percent | Response Count
< 21 Ω-M | < 21 Ω-M | 11.4% | 4
21 Ω-M to 46 Ω-M | 21 Ω-M to 46 Ω-M | 17.1% | 6
47 Ω-M to 72 Ω-M | 47 Ω-M to 72 Ω-M | 5.7% | 2
73 Ω-M to 99 Ω-M | 73 Ω-M to 99 Ω-M | 11.4% | 4
> 100 Ω-M | > 100 Ω-M | 2.9% | 1
Other, please specify | Other, please specify | 51.4% | 18
Other (please specify) | Other (please specify) | 19 | 19
answered question | answered question | 35 | 35
skipped question | skipped question | 70 | 70
Number | Response Date | Other (please specify)
1 | 2009-06-09 01:13 | not covered yet
2 | 2009-06-09 16:53 | Do not assume concrete as a grounding material
3 | 2009-06-09 17:40 | don't know
4 | 2009-06-10 08:20 | Treat wet concrete as native soil
5 | 2009-06-10 08:59 | We dont use concrete floors
6 | 2009-06-10 13:08 | don't use concrete
7 | 2009-06-10 17:21 | N/A
8 | 2009-06-15 05:47 | Dont apply
9 | 2009-06-15 17:44 | Don't use concrete in calculations
10 | 2009-06-16 20:10 | Do not specify.
11 | 2009-06-17 14:29 | do not use concrete
12 | 2009-06-18 12:11 | when considered, we assume it is the same resistivity as the underlying soil - usually a few hundred ohm-m
13 | 2009-06-29 18:14 | 30 to 90 ohm-meters
14 | 2009-06-30 05:26 | Dpn't use concrete as surface material
15 | 2009-06-30 13:18 | not used
16 | 2009-07-02 20:54 | No particular value is specified.
17 | 2009-07-09 21:24 | we do not consider concrete as part of the earthing system - as it is hygroscopic.
18 | 2009-07-20 03:11 | The same as the native soil.
19 | 2009-08-10 19:46 | Ignore concrete and treat as equal to native soil value.

## Part 2_Question 22
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
What range of wet "Asphalt" resistivity values do you use? | What range of wet "Asphalt" resistivity values do you use? | What range of wet "Asphalt" resistivity values do you use? | What range of wet "Asphalt" resistivity values do you use?
Answer Options | Answer Options | Response Percent | Response Count
< 10,000 Ω-M | < 10,000 Ω-M | 32.4% | 12
10,000 Ω-M to 999,999 Ω-M | 10,000 Ω-M to 999,999 Ω-M | 32.4% | 12
1,000,000 Ω-M to 2,999,999 Ω-M | 1,000,000 Ω-M to 2,999,999 Ω-M | 2.7% | 1
3,000,000 Ω-M to 5,999,999 Ω-M | 3,000,000 Ω-M to 5,999,999 Ω-M | 0% | 0
> 6,000,000 Ω-M | > 6,000,000 Ω-M | 2.7% | 1
Other, please specify | Other, please specify | 29.7% | 11
Other (please specify) | Other (please specify) | 12 | 12
answered question | answered question | 37 | 37
skipped question | skipped question | 68 | 68
Number | Response Date | Other (please specify)
1 | 2009-06-09 01:13 | Not covered
2 | 2009-06-09 17:40 | don't know
3 | 2009-06-10 08:59 | Not used
4 | 2009-06-10 13:08 | don't use asphalt
5 | 2009-06-10 17:21 | N/A
6 | 2009-06-15 05:47 | Dont apply
7 | 2009-06-15 17:44 | Assume 10,000 ohm-m
8 | 2009-06-16 20:10 | Do No specifiy.
9 | 2009-06-17 14:29 | do not use asphalt
10 | 2009-06-30 13:18 | not used
11 | 2009-07-09 21:24 | 3000
12 | 2009-08-10 19:46 | Treat same as crushed rock.

## Part 2_Question 23
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 2: Calculated values and reference values used to determine the adequacy of the design:
Do you use IEEE Std 80 values for the "Typical Surface Material Resistivities" as shown on the table in Section 13.1? | Do you use IEEE Std 80 values for the "Typical Surface Material Resistivities" as shown on the table in Section 13.1? | Do you use IEEE Std 80 values for the "Typical Surface Material Resistivities" as shown on the table in Section 13.1? | Do you use IEEE Std 80 values for the "Typical Surface Material Resistivities" as shown on the table in Section 13.1?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 62.3% | 43
No | No | 37.7% | 26
answered question | answered question | 69 | 69
skipped question | skipped question | 36 | 36

## Part 3_Question 1
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
Is the substation fence connected to the ground grid? | Is the substation fence connected to the ground grid? | Is the substation fence connected to the ground grid? | Is the substation fence connected to the ground grid?
Answer Options | Answer Options | Response Percent | Response Count
Always | Always | 69.2% | 45
Never | Never | 7.7% | 5
Sometimes, please give reasons: | Sometimes, please give reasons: | 26.2% | 17
Other (please specify) | Other (please specify) | 17 | 17
answered question | answered question | 65 | 65
skipped question | skipped question | 40 | 40
Number | Response Date | Other (please specify)
1 | 2009-06-09 13:07 | Older substations, ~1960's vintage, are not.
2 | 2009-06-09 13:22 | older designed substations did not include fence in grid design
3 | 2009-06-09 15:14 | In following examples: DS to control fence voltage For cases we have shortage of space For cases we extend grid over the fence For COGEN cases that two properties have common border Some cases with high resistivity of soil to help bring down GPR
4 | 2009-06-10 08:26 | It depends on the touch voltage requirement.
5 | 2009-06-10 09:12 | The boundary fence is sometimes unearthed (floating) to reduce transferred potential especially when farmers etc. connect their fence to our boundary fence. The substation safety fence is always earthed.
6 | 2009-06-15 05:26 | Depends on distance between fence and grid. ETSA prefers to have a grounding ring (attached to the grid and the fence) approx 1m outside of the substation fence. This is not always practical and if the fence is far enough away from the grid, the fence will be earthed separately.
7 | 2009-06-17 12:23 | For large substations, typically at 500kV, we do not connect the substation fence to the substation ground grid for economic reasons. We will have a separate fence ground. The fence is grounded, just not to the substation ground grid.
8 | 2009-06-18 12:21 | almostr always, but might be separately grounded if very far away from internal structures
9 | 2009-06-22 15:19 | depends on the size of the fenced station area in comparison to the equipment/structure footprint
10 | 2009-06-23 09:11 | in most of the situation as we are dealing with high on low soil resistivity and cater for arial condcutor breakage
11 | 2009-06-29 18:50 | Depending on the GPR value of the station.
12 | 2009-06-29 21:56 | New designs always, older designs sometimes based on age
13 | 2009-06-30 14:46 | when there is close proximity to substation equipment, when connected to third party generating station, sometimes used to reduce grid resistance and lower the GPR value.
14 | 2009-07-09 21:31 | Depending on proximity of neighbours, and the available site realestate for grading rings, isolation zones etc.
15 | 2009-07-13 18:33 | Depends upon fence proximity to substation ground grid.
16 | 2009-07-14 15:05 | When we are in shortage of space, When we counter poise to adjacent grid When we have high fence potential
17 | 2009-08-10 19:52 | For new designs, yes. For existing designs, often leave as is, unless can make argument for connecting.

## Part 3_Question 2
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
Do you run a dedicated grounding conductor to the following fence and gate components? | Do you run a dedicated grounding conductor to the following fence and gate components? | Do you run a dedicated grounding conductor to the following fence and gate components? | Do you run a dedicated grounding conductor to the following fence and gate components? | Do you run a dedicated grounding conductor to the following fence and gate components?
Answer Options | Answer Options | Yes | No | Response Count
Fabric | Fabric | 31 | 23 | 54
Posts | Posts | 61 | 1 | 61
Swing Gate | Swing Gate | 61 | 0 | 61
Rolling Gate | Rolling Gate | 47 | 6 | 53
Top Rail | Top Rail | 27 | 23 | 50
Barb Wire | Barb Wire | 38 | 20 | 58
answered question | answered question | answered question | 64 | 64
skipped question | skipped question | skipped question | 41 | 41

## Part 3_Question 3
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
If "YES" to questions in 2, what conductor size do you use to connect to the following? | If "YES" to questions in 2, what conductor size do you use to connect to the following? | If "YES" to questions in 2, what conductor size do you use to connect to the following? | If "YES" to questions in 2, what conductor size do you use to connect to the following? | If "YES" to questions in 2, what conductor size do you use to connect to the following? | If "YES" to questions in 2, what conductor size do you use to connect to the following? | If "YES" to questions in 2, what conductor size do you use to connect to the following? | If "YES" to questions in 2, what conductor size do you use to connect to the following? | If "YES" to questions in 2, what conductor size do you use to connect to the following? | If "YES" to questions in 2, what conductor size do you use to connect to the following? | If "YES" to questions in 2, what conductor size do you use to connect to the following?
AWG | AWG | AWG | AWG | AWG | AWG | AWG | AWG | AWG | AWG | AWG
Answer Options | Answer Options | 6 | 4 | 2 | 1 | 1/0 | 2/0 | 4/0 | 250 | Response Count
Fabric | Fabric | 6 | 4 | 6 | 0 | 2 | 6 | 1 | 0 | 25
Posts | Posts | 0 | 3 | 1 | 0 | 4 | 7 | 26 | 0 | 41
Swing Gate | Swing Gate | 1 | 3 | 3 | 0 | 3 | 10 | 16 | 2 | 38
Rolling Gate | Rolling Gate | 1 | 2 | 3 | 0 | 2 | 8 | 17 | 1 | 34
Top Rail | Top Rail | 2 | 3 | 6 | 0 | 3 | 3 | 4 | 0 | 21
Barb Wire | Barb Wire | 5 | 6 | 7 | 0 | 2 | 4 | 2 | 2 | 28
Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² )
Answer Options | Answer Options | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 240 | Response Count
Fabric | Fabric | 1 | 0 | 0 | 0 | 2 | 2 | 1 | 0 | 6
Posts | Posts | 1 | 0 | 0 | 0 | 7 | 3 | 3 | 0 | 14
Swing Gate | Swing Gate | 1 | 0 | 0 | 0 | 8 | 3 | 2 | 1 | 15
Rolling Gate | Rolling Gate | 0 | 0 | 0 | 0 | 4 | 3 | 1 | 1 | 9
Top Rail | Top Rail | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 4
Barb Wire | Barb Wire | 0 | 0 | 0 | 0 | 4 | 2 | 1 | 0 | 7
[9 empty] | Question Totals | Question Totals
Other (specify which location) | Other (specify which location) | Other (specify which location) | Other (specify which location) | Other (specify which location) | Other (specify which location) | Other (specify which location) | Other (specify which location) | Other (specify which location) | 11 | 11
answered question | answered question | answered question | answered question | answered question | answered question | answered question | answered question | answered question | 59 | 59
skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | 46 | 46
Number | Response Date | Other (specify which location)
1 | 2009-06-09 11:44 | We also use flexible copper braids for gates
2 | 2009-06-09 13:22 | #2 or larger
3 | 2009-06-10 09:12 | Multiple connections of 70mm2
4 | 2009-06-11 08:24 | 5.5mm2
5 | 2009-06-14 22:35 | same as buried grid conductor
6 | 2009-06-15 05:53 | 70mm is the minimum. May be higher to suit the site fault level.
7 | 2009-06-18 12:21 | posts are 2/0 minimum - sized same as other risers based on fault current
8 | 2009-06-18 23:16 | posts 134mm^2
9 | 2009-06-30 13:24 | 8 to fabric and to barb wire and top rail
10 | 2009-07-01 03:12 | Where required - 120 sq mm - in high restive soil
11 | 2009-07-02 21:02 | Unsure.

## Part 3_Question 4
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
If "YES" to questions in 2, what is the conductor interval spacing? | If "YES" to questions in 2, what is the conductor interval spacing? | If "YES" to questions in 2, what is the conductor interval spacing? | If "YES" to questions in 2, what is the conductor interval spacing? | If "YES" to questions in 2, what is the conductor interval spacing? | If "YES" to questions in 2, what is the conductor interval spacing? | If "YES" to questions in 2, what is the conductor interval spacing? | If "YES" to questions in 2, what is the conductor interval spacing? | If "YES" to questions in 2, what is the conductor interval spacing?
Feet | Feet | Feet | Feet | Feet | Feet | Feet | Feet | Feet
Answer Options | Answer Options | 10 | 20 | 30 | 40 | 50 | 100 | Response Count
Fabric | Fabric | 1 | 2 | 1 | 7 | 9 | 1 | 21
Posts | Posts | 2 | 7 | 3 | 9 | 13 | 1 | 35
Top Rail | Top Rail | 1 | 4 | 1 | 6 | 7 | 0 | 19
Barb Wire | Barb Wire | 0 | 4 | 1 | 7 | 9 | 3 | 24
Meters | Meters | Meters | Meters | Meters | Meters | Meters | Meters | Meters
Answer Options | Answer Options | 3 | 6 | 9 | 12 | 15 | 30 | Response Count
Fabric | Fabric | 0 | 2 | 0 | 1 | 0 | 1 | 4
Posts | Posts | 0 | 6 | 0 | 3 | 5 | 1 | 15
Top Rail | Top Rail | 0 | 4 | 0 | 0 | 1 | 0 | 5
Barb Wire | Barb Wire | 0 | 3 | 0 | 2 | 1 | 1 | 7
[7 empty] | Question Totals | Question Totals
Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | 14 | 14
answered question | answered question | answered question | answered question | answered question | answered question | answered question | 52 | 52
skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | 53 | 53
Number | Response Date | Other (please specify)
1 | 2009-06-08 22:24 | Depends on grid spacing
2 | 2009-06-09 11:44 | Varies from 10 feet and up depending on design.
3 | 2009-06-10 09:12 | connected every 20m
4 | 2009-06-11 08:24 | 5.5mm2
5 | 2009-06-12 11:52 | No not know the details
6 | 2009-06-15 05:26 | Approximate value
7 | 2009-06-15 22:48 | Every alternate post
8 | 2009-06-17 12:23 | 75 feet maxium interval for fabric, posts, top rail, and barb wire
9 | 2009-06-18 12:21 | at all corner and pull posts, then at 30-50 ft intervals
10 | 2009-06-29 17:28 | 75 feet apart
11 | 2009-06-30 14:46 | Posts are grounded at corners and every 75' in between
12 | 2009-07-01 03:12 | 8 to 10 m
13 | 2009-07-02 21:02 | Fabric and posts bonded at least every 20 metres.
14 | 2009-07-21 15:16 | 75'

## Part 3_Question 5
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
Is the fence inside or outside the ground grid perimeter? | Is the fence inside or outside the ground grid perimeter? | Is the fence inside or outside the ground grid perimeter? | Is the fence inside or outside the ground grid perimeter? | Is the fence inside or outside the ground grid perimeter? | Is the fence inside or outside the ground grid perimeter?
Answer Options | Answer Options | Always | Never | Typically | Response Count
Inside | Inside | 27 | 1 | 24 | 52
Outside | Outside | 6 | 8 | 8 | 22
answered question | answered question | answered question | answered question | 64 | 64
skipped question | skipped question | skipped question | skipped question | 41 | 41

## Part 3_Question 6
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
Do you install a fence perimeter ground grid conductor outside the fence, if the fence is not bonded to the ground grid? | Do you install a fence perimeter ground grid conductor outside the fence, if the fence is not bonded to the ground grid? | Do you install a fence perimeter ground grid conductor outside the fence, if the fence is not bonded to the ground grid? | Do you install a fence perimeter ground grid conductor outside the fence, if the fence is not bonded to the ground grid?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 53.2% | 25
No | No | 46.8% | 22
answered question | answered question | 47 | 47
skipped question | skipped question | 58 | 58

## Part 3_Question 7
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
Do you control the step and touch potential voltages within the full swing of all gates? | Do you control the step and touch potential voltages within the full swing of all gates? | Do you control the step and touch potential voltages within the full swing of all gates? | Do you control the step and touch potential voltages within the full swing of all gates?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 93.8% | 60
No | No | 6.3% | 4
answered question | answered question | 64 | 64
skipped question | skipped question | 41 | 41

## Part 3_Question 8
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
Do you take extra precautions to control surface gradients at the handle of disconnect switches? | Do you take extra precautions to control surface gradients at the handle of disconnect switches? | Do you take extra precautions to control surface gradients at the handle of disconnect switches? | Do you take extra precautions to control surface gradients at the handle of disconnect switches?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 81% | 51
No | No | 12.7% | 8
Sometimes, please explain below | Sometimes, please explain below | 6.3% | 4
Sometimes (please specify) | Sometimes (please specify) | 8 | 8
answered question | answered question | 63 | 63
skipped question | skipped question | 42 | 42
Number | Response Date | Sometimes (please specify)
1 | 2009-06-09 16:58 | Surface gradients are checked and remediated as necessary.
2 | 2009-06-10 09:12 | Sometimes equipotential grids are used
3 | 2009-06-12 11:52 | Installed grounded platforms are usually needed already due to the height.
4 | 2009-06-15 17:52 | Bond switch handles to structure. Line switches use raised platform
5 | 2009-06-29 20:11 | For manually operated, high voltage disconnect switches a grounding pad is installed for the operator to stand on.
6 | 2009-06-29 21:56 | Typically no, but there are some exceptions in some parts of the company.
7 | 2009-06-30 14:46 | All switches inside station get switch platforms made of steel bonded to the switch handle
8 | 2009-08-10 19:52 | Switch mat.

## Part 3_Question 9
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
If "YES" to the prior question, please select method: | If "YES" to the prior question, please select method: | If "YES" to the prior question, please select method: | If "YES" to the prior question, please select method:
Answer Options | Answer Options | Response Percent | Response Count
Installed wire mesh | Installed wire mesh | 49.1% | 27
Installed grounded platform | Installed grounded platform | 60% | 33
Installed insulated platform | Installed insulated platform | 1.8% | 1
Change spacing of primary grid | Change spacing of primary grid | 10.9% | 6
Other | Other | 5.5% | 3
Other (please specify) | Other (please specify) | 8 | 8
answered question | answered question | 55 | 55
skipped question | skipped question | 50 | 50
Number | Response Date | Other (please specify)
1 | 2009-06-09 15:14 | Direct connect to grid through Multi Rev device
2 | 2009-06-15 05:26 | We have used insulated platforms in very limited number of instances, but not usually.
3 | 2009-06-15 17:52 | Line switches only
4 | 2009-06-15 22:48 | The operators mat is connected to the operator handle. The mat is not connected to the grid
5 | 2009-06-23 09:11 | Earth Mat
6 | 2009-06-30 14:46 | Switch platform on concrete block, bonded to switch handle. Structure ground is kept separated from this system.
7 | 2009-07-01 03:12 | Below Ground Operator Gradient Loops at 150mmm below surface.
8 | 2009-07-09 21:31 | On concrete surfaces we install a metal 1.5m x 1.0m plate at each disconnector (bonded to the earthgrid and disconnector handle) to manage touch potentials.

## Part 3_Question 10
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
What material is used for ground rods, main ground grid conductors, and ground grid riser conductors? | What material is used for ground rods, main ground grid conductors, and ground grid riser conductors? | What material is used for ground rods, main ground grid conductors, and ground grid riser conductors? | What material is used for ground rods, main ground grid conductors, and ground grid riser conductors? | What material is used for ground rods, main ground grid conductors, and ground grid riser conductors? | What material is used for ground rods, main ground grid conductors, and ground grid riser conductors?
Answer Options | Answer Options | Ground Rods | Ground Grid Conductor | Ground Grid Riser Conductor | Response Count
Copper | Copper | 26 | 63 | 54 | 63
Copper Bonded Steel | Copper Bonded Steel | 42 | 4 | 13 | 43
Galvanized Steel | Galvanized Steel | 3 | 2 | 1 | 4
Stainless Steel | Stainless Steel | 2 | 0 | 0 | 2
Other | Other | 1 | 2 | 5 | 7
Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | 7 | 7
answered question | answered question | answered question | answered question | 65 | 65
skipped question | skipped question | skipped question | skipped question | 40 | 40
Number | Response Date | Other (please specify)
1 | 2009-06-09 12:43 | Typically use tinned 2/0 copper conductor for fence grounds.
2 | 2009-06-09 15:14 | Alluminum Alloy
3 | 2009-06-10 13:22 | We still have some legacy cathodically-protected "black steel" ground grids installed during WWII era when copper was rationed/unavailable. In addition, during a timeframe when copper theft was on a rise, we changed standards to specify copper-clad steel for ground grid and riser conductor. However, our standards have been all copper for about 15 years now.
4 | 2009-06-15 05:26 | ETSA uses a standard 3m stainless steel rod for earthing of domestic installations, distribution transformers, steel/concrete distribution poles etc. These rods are also commonly used in our substations. Deeper rods are copper or copper bonded.
5 | 2009-06-15 17:52 | Copperweld
6 | 2009-06-29 18:50 | steel for ground rods.
7 | 2009-07-14 15:05 | Aluminum Alloy

## Part 3_Question 11
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
What is the size of the ground grid conductors used? | What is the size of the ground grid conductors used? | What is the size of the ground grid conductors used? | What is the size of the ground grid conductors used? | What is the size of the ground grid conductors used? | What is the size of the ground grid conductors used? | What is the size of the ground grid conductors used? | What is the size of the ground grid conductors used? | What is the size of the ground grid conductors used? | What is the size of the ground grid conductors used? | What is the size of the ground grid conductors used?
AWG | AWG | AWG | AWG | AWG | AWG | AWG | AWG | AWG | AWG | AWG
Answer Options | Answer Options | 1/0 | 2/0 | 3/0 | 4/0 | 250 | 300 | 350 | 500 | Response Count
Minimum | Minimum | 2 | 14 | 0 | 25 | 2 | 0 | 0 | 0 | 43
Maximum | Maximum | 0 | 1 | 0 | 7 | 2 | 0 | 4 | 28 | 42
Most Common | Most Common | 0 | 2 | 0 | 34 | 2 | 1 | 2 | 1 | 42
Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² ) | Metric ( mm² )
Answer Options | Answer Options | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300 | Response Count
Minimum | Minimum | 2 | 5 | 4 | 3 | 1 | 0 | 0 | 0 | 15
Maximum | Maximum | 0 | 1 | 2 | 6 | 1 | 0 | 3 | 0 | 13
Most Common | Most Common | 0 | 4 | 5 | 2 | 0 | 2 | 0 | 0 | 13
[9 empty] | Question Totals | Question Totals
Other (please specify material and size) | Other (please specify material and size) | Other (please specify material and size) | Other (please specify material and size) | Other (please specify material and size) | Other (please specify material and size) | Other (please specify material and size) | Other (please specify material and size) | Other (please specify material and size) | 8 | 8
answered question | answered question | answered question | answered question | answered question | answered question | answered question | answered question | answered question | 59 | 59
skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | 46 | 46
Number | Response Date | Other (please specify material and size)
1 | 2009-06-10 09:12 | multiples of 2 x 70mm2 for risers depending on fault levels, 70mm2 used for main grid, and ground rods can be any size from 70mm2 upwards depending on the contractor.
2 | 2009-06-11 08:24 | 60~100x2 mm2
3 | 2009-06-12 11:52 | 400 kV/95 mm2, 110 kV/25 mm2
4 | 2009-06-15 05:26 | Copper flat bar 20x3 or 40x4mm
5 | 2009-06-15 22:48 | Maximum conductor size is dictated by substation max fault current
6 | 2009-06-18 12:21 | based on available fault current for distribution stations; use 4/0 for all generation and transmission subs
7 | 2009-07-02 21:02 | Depends on calculated fault current and duration.
8 | 2009-08-31 00:44 | Galvanized Steel 640mm2

## Part 3_Question 12
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
How do you determine the size of the main ground grid conductor? | How do you determine the size of the main ground grid conductor? | How do you determine the size of the main ground grid conductor? | How do you determine the size of the main ground grid conductor?
Answer Options | Answer Options | Response Percent | Response Count
Available short circuit and fault duration | Available short circuit and fault duration | 63.5% | 40
Standard size based on company standards | Standard size based on company standards | 69.8% | 44
Mechanical strength | Mechanical strength | 15.9% | 10
answered question | answered question | 63 | 63
skipped question | skipped question | 42 | 42

## Part 3_Question 13
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
How do you determine the size of the risers that join the main ground grid to the equipment and structures? | How do you determine the size of the risers that join the main ground grid to the equipment and structures? | How do you determine the size of the risers that join the main ground grid to the equipment and structures? | How do you determine the size of the risers that join the main ground grid to the equipment and structures?
Answer Options | Answer Options | Response Percent | Response Count
Available short circuit and fault duration | Available short circuit and fault duration | 56.3% | 36
Standard size based on company standards | Standard size based on company standards | 67.2% | 43
Mechanical strength | Mechanical strength | 15.6% | 10
answered question | answered question | 64 | 64
skipped question | skipped question | 41 | 41

## Part 3_Question 14
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
What type of connectors are generally used to connect: | What type of connectors are generally used to connect: | What type of connectors are generally used to connect: | What type of connectors are generally used to connect: | What type of connectors are generally used to connect: | What type of connectors are generally used to connect: | What type of connectors are generally used to connect: | What type of connectors are generally used to connect:
Answer Options | Answer Options | Exothermic Connection | Brazed Connection | Compression Connection | Bolted Connection | Other | Response Count
Intersecting below grade ground grid conductors | Intersecting below grade ground grid conductors | 50 | 5 | 19 | 4 | 1 | 62
Metallic fence post to ground grid riser | Metallic fence post to ground grid riser | 14 | 4 | 11 | 42 | 2 | 61
Metallic structure to ground grid riser | Metallic structure to ground grid riser | 15 | 4 | 12 | 40 | 2 | 62
Equipment to ground grid riser | Equipment to ground grid riser | 11 | 3 | 14 | 49 | 1 | 62
Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | Other (please specify) | 4 | 4
answered question | answered question | answered question | answered question | answered question | answered question | 62 | 62
skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | 43 | 43
Number | Response Date | Other (please specify)
1 | 2009-06-10 13:22 | We had used exothermic connections exclusively up until the commercial introduction and industry acceptance of the shear-bolt "wedge-type" connector. The latter is most often used for all below-grade ground connections though exothermic remains an approved method.
2 | 2009-06-15 17:52 | May use Cadwel bar lug for equipment ground
3 | 2009-06-23 09:11 | But we are going to change to Exothermic for underground
4 | 2009-06-29 20:11 | cadweld

## Part 3_Question 15
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
is the reinforcing steel bar in the substation foundations intentionally connected to the grounding grid? | is the reinforcing steel bar in the substation foundations intentionally connected to the grounding grid? | is the reinforcing steel bar in the substation foundations intentionally connected to the grounding grid? | is the reinforcing steel bar in the substation foundations intentionally connected to the grounding grid?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 25% | 15
No | No | 58.3% | 35
Sometimes, please explain | Sometimes, please explain | 16.7% | 10
Sometimes (please specify) | Sometimes (please specify) | 10 | 10
answered question | answered question | 60 | 60
skipped question | skipped question | 45 | 45
Number | Response Date | Sometimes (please specify)
1 | 2009-06-09 15:14 | IN GIS station
2 | 2009-06-10 09:12 | If theft of copper is a problem, we use the HD bolts and rebar as part of the connection, and make the connection to main earthmat below ground level from the side of the foundation. This applies if the fault levels are low enough to prevent heating and damege to the concrete.
3 | 2009-06-10 13:22 | Our foundation standard details specify a rebar grounding tail be brought out and extended to the main grid for connection. However, this is generally only done at our larger regional and bulk power facilities.
4 | 2009-06-15 05:26 | Earthed where it is possible for a person to stand on the foundation/footing.
5 | 2009-06-15 22:48 | For areas greater then 2 sq metres
6 | 2009-06-18 23:16 | buildings and operational platforms only
7 | 2009-06-30 01:01 | Only for large footings
8 | 2009-07-02 21:02 | Yes for substation buildings; otherwise no.
9 | 2009-07-08 14:01 | Under reactors with high magnetic fields, care is taken to avoid closed loops.
10 | 2009-07-08 23:53 | For buildings

## Part 3_Question 16
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
During "New Construction", do you conduct field tests on the substation grounding system? | During "New Construction", do you conduct field tests on the substation grounding system? | During "New Construction", do you conduct field tests on the substation grounding system? | During "New Construction", do you conduct field tests on the substation grounding system?
Answer Options | Answer Options | Response Percent | Response Count
YES | YES | 64.5% | 40
NO | NO | 19.4% | 12
YES and NO | YES and NO | 16.1% | 10
answered question | answered question | 62 | 62
skipped question | skipped question | 43 | 43

## Part 3_Question 17
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
If "YES" to the prior question on "New Construction", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "New Construction", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "New Construction", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "New Construction", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "New Construction", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "New Construction", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "New Construction", what field tests on the substation grounding system do you conduct?
Answer Options | Answer Options | Ground Grid Resistance | Step and Touch Voltages | Current Splits | Ground Grid Integrity | Response Count
Generation | Generation | 30 | 10 | 1 | 15 | 32
Transmission | Transmission | 46 | 21 | 7 | 24 | 48
Distribution | Distribution | 38 | 11 | 1 | 17 | 39
Industrial | Industrial | 21 | 4 | 1 | 12 | 22
answered question | answered question | answered question | answered question | answered question | 50 | 50
skipped question | skipped question | skipped question | skipped question | skipped question | 55 | 55

## Part 3_Question 18
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
During a "Retrofit Project", do you conduct field tests on the substation grounding system? | During a "Retrofit Project", do you conduct field tests on the substation grounding system? | During a "Retrofit Project", do you conduct field tests on the substation grounding system? | During a "Retrofit Project", do you conduct field tests on the substation grounding system?
Answer Options | Answer Options | Response Percent | Response Count
YES | YES | 33.9% | 21
NO | NO | 33.9% | 21
YES and NO | YES and NO | 32.3% | 20
answered question | answered question | 62 | 62
skipped question | skipped question | 43 | 43

## Part 3_Question 19
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
If "YES" to the prior question on "Retrofit Projects", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "Retrofit Projects", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "Retrofit Projects", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "Retrofit Projects", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "Retrofit Projects", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "Retrofit Projects", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "Retrofit Projects", what field tests on the substation grounding system do you conduct?
Answer Options | Answer Options | Ground Grid Resistance | Step and Touch Potential | Current Splits | Ground Grid Integrity | Response Count
Generation | Generation | 22 | 8 | 4 | 16 | 26
Transmission | Transmission | 32 | 15 | 7 | 25 | 40
Distribution | Distribution | 26 | 9 | 1 | 19 | 33
Industrial | Industrial | 15 | 6 | 3 | 13 | 20
answered question | answered question | answered question | answered question | answered question | 40 | 40
skipped question | skipped question | skipped question | skipped question | skipped question | 65 | 65

## Part 3_Question 20
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
During a "Failed Equipment Change-Out", do you conduct field tests on the substation grounding system? | During a "Failed Equipment Change-Out", do you conduct field tests on the substation grounding system? | During a "Failed Equipment Change-Out", do you conduct field tests on the substation grounding system? | During a "Failed Equipment Change-Out", do you conduct field tests on the substation grounding system?
Answer Options | Answer Options | Response Percent | Response Count
YES | YES | 11.5% | 7
NO | NO | 67.2% | 41
YES and NO | YES and NO | 21.3% | 13
answered question | answered question | 61 | 61
skipped question | skipped question | 44 | 44

## Part 3_Question 21
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 3: Practices during and after installation of the grounding system
If "YES" to the prior question on "Failed Equipment Change-Outs", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "Failed Equipment Change-Outs", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "Failed Equipment Change-Outs", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "Failed Equipment Change-Outs", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "Failed Equipment Change-Outs", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "Failed Equipment Change-Outs", what field tests on the substation grounding system do you conduct? | If "YES" to the prior question on "Failed Equipment Change-Outs", what field tests on the substation grounding system do you conduct?
Answer Options | Answer Options | Ground Grid Resistance | Step and Touch Voltage | Current Splits | Ground Grid Integrity | Response Count
Generation | Generation | 7 | 5 | 1 | 13 | 14
Transmission | Transmission | 9 | 6 | 2 | 15 | 17
Distribution | Distribution | 9 | 5 | 0 | 12 | 16
Industrial | Industrial | 7 | 5 | 2 | 12 | 13
answered question | answered question | answered question | answered question | answered question | 17 | 17
skipped question | skipped question | skipped question | skipped question | skipped question | 88 | 88

## Part 4_Question 1
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 4: Hazards and/or accidents related to grounding
In the last ten years, have there been any electrocutions due to step, touch, transferred voltages, inside and/or outside the substation fence? | In the last ten years, have there been any electrocutions due to step, touch, transferred voltages, inside and/or outside the substation fence? | In the last ten years, have there been any electrocutions due to step, touch, transferred voltages, inside and/or outside the substation fence? | In the last ten years, have there been any electrocutions due to step, touch, transferred voltages, inside and/or outside the substation fence?
Answer Options | Answer Options | Response Percent | Response Count
YES | YES | 8.1% | 5
NO | NO | 91.9% | 57
YES and NO | YES and NO | 0% | 0
answered question | answered question | 62 | 62
skipped question | skipped question | 43 | 43

## Part 4_Question 2
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 4: Hazards and/or accidents related to grounding
If "YES" to the prior question on electrocutions, please select locations. | If "YES" to the prior question on electrocutions, please select locations. | If "YES" to the prior question on electrocutions, please select locations. | If "YES" to the prior question on electrocutions, please select locations. | If "YES" to the prior question on electrocutions, please select locations. | If "YES" to the prior question on electrocutions, please select locations. | If "YES" to the prior question on electrocutions, please select locations. | If "YES" to the prior question on electrocutions, please select locations. | If "YES" to the prior question on electrocutions, please select locations.
Answer Options | Answer Options | Inside the Fence - Step Voltages | Inside the Fence - Touch Voltages | Inside the Fence - Transfer Voltages | Outside the Fence - Step Voltages | Outside the Fence - Touch Voltages | Outside the Fence - Transfer Voltages | Response Count
Generation | Generation | 0 | 1 | 0 | 0 | 0 | 0 | 1
Transmission | Transmission | 0 | 2 | 2 | 0 | 0 | 0 | 4
Distribution | Distribution | 0 | 1 | 0 | 1 | 0 | 0 | 2
Industrial | Industrial | 0 | 1 | 0 | 0 | 0 | 0 | 1
answered question | answered question | answered question | answered question | answered question | answered question | answered question | 5 | 5
skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | skipped question | 100 | 100

## Part 5_Question 1
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 5: Comments on the present edition of the Guide #80
How familiar are you with the IEEE Guide 80-2000, "Guide for Safety in AC Substation Grounding"? | How familiar are you with the IEEE Guide 80-2000, "Guide for Safety in AC Substation Grounding"? | How familiar are you with the IEEE Guide 80-2000, "Guide for Safety in AC Substation Grounding"? | How familiar are you with the IEEE Guide 80-2000, "Guide for Safety in AC Substation Grounding"?
Answer Options | Answer Options | Response Percent | Response Count
I have never heard about this guide before | I have never heard about this guide before | 3.1% | 2
I knew about the existence of the guide, but I do not use it in my work | I knew about the existence of the guide, but I do not use it in my work | 10.9% | 7
The company has it's own guide | The company has it's own guide | 20.3% | 13
We are using the Guide 80 | We are using the Guide 80 | 81.3% | 52
answered question | answered question | 64 | 64
skipped question | skipped question | 41 | 41

## Part 6_Question 1
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 6: Comments on the present edition of the Std 837
How familiar are you with the IEEE Std 837-2002, "Standard for Qualifying Permanent Connection Used in Substation Grounding"? | How familiar are you with the IEEE Std 837-2002, "Standard for Qualifying Permanent Connection Used in Substation Grounding"? | How familiar are you with the IEEE Std 837-2002, "Standard for Qualifying Permanent Connection Used in Substation Grounding"? | How familiar are you with the IEEE Std 837-2002, "Standard for Qualifying Permanent Connection Used in Substation Grounding"?
Answer Options | Answer Options | Response Percent | Response Count
I have never heard about this standard before | I have never heard about this standard before | 12.9% | 8
I knew about the existence of the standard, but I do not use it in my work. | I knew about the existence of the standard, but I do not use it in my work. | 29% | 18
The company has it's own standard | The company has it's own standard | 22.6% | 14
We are following the Standard 837 | We are following the Standard 837 | 50% | 31
answered question | answered question | 62 | 62
skipped question | skipped question | 43 | 43

## Part 7_Question 1
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 7: Connection selection criteria, theory, and assumptions
Do you require your grounding connectors to comply with IEEE Std 837? | Do you require your grounding connectors to comply with IEEE Std 837? | Do you require your grounding connectors to comply with IEEE Std 837? | Do you require your grounding connectors to comply with IEEE Std 837?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 61.4% | 35
No | No | 38.6% | 22
answered question | answered question | 57 | 57
skipped question | skipped question | 48 | 48

## Part 7_Question 2
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 7: Connection selection criteria, theory, and assumptions
Do you make your substation grounding connector selection based on IEEE Std 837 compliance test documents? | Do you make your substation grounding connector selection based on IEEE Std 837 compliance test documents? | Do you make your substation grounding connector selection based on IEEE Std 837 compliance test documents? | Do you make your substation grounding connector selection based on IEEE Std 837 compliance test documents?
Answer Options | Answer Options | Response Percent | Response Count
3rd Party Test | 3rd Party Test | 23.4% | 11
Manufacturer Test | Manufacturer Test | 53.2% | 25
In-House Test | In-House Test | 23.4% | 11
answered question | answered question | 47 | 47
skipped question | skipped question | 58 | 58

## Part 7_Question 3
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 7: Connection selection criteria, theory, and assumptions
When selecting a substation grounding connector style, do you use the same evaluation criteria for both above and below grade connections used in the grounding electrode system? | When selecting a substation grounding connector style, do you use the same evaluation criteria for both above and below grade connections used in the grounding electrode system? | When selecting a substation grounding connector style, do you use the same evaluation criteria for both above and below grade connections used in the grounding electrode system? | When selecting a substation grounding connector style, do you use the same evaluation criteria for both above and below grade connections used in the grounding electrode system?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 38.6% | 22
No | No | 61.4% | 35
answered question | answered question | 57 | 57
skipped question | skipped question | 48 | 48

## Part 7_Question 4
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 7: Connection selection criteria, theory, and assumptions
During a retrofit construction project, and when joining a new grounding grid to an existing and presumably much older grounding grid, are any special considerations given to the connection between the two ground grids? | During a retrofit construction project, and when joining a new grounding grid to an existing and presumably much older grounding grid, are any special considerations given to the connection between the two ground grids? | During a retrofit construction project, and when joining a new grounding grid to an existing and presumably much older grounding grid, are any special considerations given to the connection between the two ground grids? | During a retrofit construction project, and when joining a new grounding grid to an existing and presumably much older grounding grid, are any special considerations given to the connection between the two ground grids?
Answer Options | Answer Options | Response Percent | Response Count
Yes | Yes | 38.6% | 22
No | No | 61.4% | 35
answered question | answered question | 57 | 57
skipped question | skipped question | 48 | 48

## Part 7_Question 5
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 7: Connection selection criteria, theory, and assumptions
If "YES" to the prior question, what are the special considerations? | If "YES" to the prior question, what are the special considerations? | If "YES" to the prior question, what are the special considerations?
Answer Options | Answer Options | Response Count
23
answered question | 23 | 23
skipped question | 82 | 82
Number | Response Date | Response Text
1 | 2009-06-08 22:26 | No - Steve
2 | 2009-06-09 01:33 | Check for coppper condition review calculation if applicable
3 | 2009-06-09 05:28 | Provide four (4) 350 Kcmil soft drawn copper connection
4 | 2009-06-09 12:45 | Check for degradation of existing ground conductor, and connectors (if found)
5 | 2009-06-09 13:24 | use of heavy duty molds
6 | 2009-06-09 15:16 | Compare manufacturer test with field test
7 | 2009-06-10 09:17 | We check the integrity of the existing grid.
8 | 2009-06-10 16:03 | consideration on integrity of existing grid and tie-in with exothermic connection
9 | 2009-06-10 17:14 | integrity of existing grid and use of exothermic connection
10 | 2009-06-10 17:30 | Isolation sections between new & old fences.
11 | 2009-06-12 11:55 | I am not able to answer to these specific questions. The safety code requires checking of the systems at regular intervals
12 | 2009-06-15 22:49 | Site fault current IEEE 837 compliant connections
13 | 2009-06-16 20:18 | Below grade connections must be exothermic type and must be thoroughly cleaned and inspected.
14 | 2009-06-18 12:24 | jumper new and old grid together prior to handling
15 | 2009-06-23 09:26 | Cleaning the joint and using Exothermic connector
16 | 2009-06-29 18:50 | Modify the existing ground grid if required.
17 | 2009-06-30 14:48 | Extra cleaning and heavy duty exothermic molds are recommended
18 | 2009-07-01 03:19 | Consideration is given to the connection conductors between the grid, the combined overall grid is modelled and current carrying capacity is checked within the new and old grid. If OK compression connectors are chosed to connect grids of different sizes.
19 | 2009-07-02 21:04 | Precautions to ensure the safety of personnel making the connections.
20 | 2009-07-08 14:02 | Circulating currents.
21 | 2009-07-09 21:35 | a number of redundant paths ( nomrmally a minimum of 4 connections are specified) - in practice the grid mesh's are normally all connected together.
22 | 2009-07-14 15:15 | I perform integrity test prior to connection to old part and I consider some depreciation factor for old part
23 | 2009-07-20 03:53 | Step and touch voltages, transferred potentials, current ratings of the old and new installations and any possible increase in faul levels.

## Part 7_Question 6
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 7: Connection selection criteria, theory, and assumptions
In the past ten years, are you aware of any grounding connection failures? | In the past ten years, are you aware of any grounding connection failures? | In the past ten years, are you aware of any grounding connection failures? | In the past ten years, are you aware of any grounding connection failures? | In the past ten years, are you aware of any grounding connection failures?
Answer Options | Answer Options | Yes | No | Response Count
Below Grade 837 Non-Compliant | Below Grade 837 Non-Compliant | 14 | 35 | 49
Below Grade 837 Compliant | Below Grade 837 Compliant | 3 | 39 | 42
Above Grade 837 Non-Compliant | Above Grade 837 Non-Compliant | 7 | 39 | 46
Above Grade 837 Compliant | Above Grade 837 Compliant | 4 | 39 | 43
answered question | answered question | answered question | 52 | 52
skipped question | skipped question | skipped question | 53 | 53

## Part 8_Question 1
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 8: Std 80 and Std 837 improvement suggestions.
Please tell us what can be added to the Std 80 that would complement your efforts. | Please tell us what can be added to the Std 80 that would complement your efforts. | Please tell us what can be added to the Std 80 that would complement your efforts.
Answer Options | Answer Options | Response Count
20
answered question | 20 | 20
skipped question | 85 | 85
Number | Response Date | Response Text
1 | 2009-06-08 22:29 | Increased focus on copper clad materials due to theft.
2 | 2009-06-09 05:32 | Man made ground well/lectrode for sandy soil
3 | 2009-06-09 12:51 | Add the following: 1. Complete example of generation grounding 2. Complete example of substation grounding 3. Complete example of distribution grounding 4. Complete example of industrial grounding
4 | 2009-06-09 12:55 | Step by Step design process recommendations. A "practical" methodology frequently followed at our utility is offered for your consideration: November 2001 Substation Ground Grid Design Procedure Background Information These substation ground grid design guidelines are based mostly upon the recently updated IEEE 80-2000 Standard entitled, “IEEE Guide for Safety in AC Substation Grounding.” Extensive review of this Standard should be the first step in the design or modification of an electric substation ground grid. Particular attention should be given to at least the following portions of the IEEE 80-2000 Standard: Section 9.4 - Basic Aspects of Grid Design, Section 9.5 - Design in Difficult Conditions, Section 16.1 - Design Criteria, Section 16.2 - Critical Parameters, Section 16.3 and Table 12 - Index of Design Parameters, Section 16.4 - Design Procedure, Section 16.5 - Calculation of Maximum Step and Mesh Voltages, Figure 33 - Design procedure block diagram, and Section 16.6 - Refinement of Preliminary Design. The Commonwealth Associates Excel spreadsheet, located on the J:\Review/IEEE drive, provides a good template for the substation ground grid design process and should be used for this exercise. Further technical information regarding grounding conductors can be referenced in “Technical Data – A Reference for The Electrical Power Industry” by Anderson Electrical Connectors. Confirm the following: ground conductor size, burial depth, length of grid conductor, grid spacing, crushed rock requirement, resistance to remote earth, and voltage rise of grid to remote earth. To a lessor degree, other references that might be consulted include the CU course notebook entitled, “Integrated Grounding System Design and Testing” and the background reference book “Power System Grounding and Transients,” both authored by Dr. A. P. Sakis Meliopoulos Soil resistivity can sometimes be a difficult number to exactly define. A contractor can be engaged to perform soil resistivity testing. Anderson Engineering (866-2741), and Palmerton and Parrish (831-3056), are two contractors currently under blanket CU contracts for these services. Typical values used at other CU substations may be a reasonable starting point too. Substation site specific factors can sometimes point the design in unusual directions. If a site has extensive rock or a high soil resistivity (above 1,000 ohm-meters), then other design options might need to be considered, like a grounding well or the use of ground enhancement material. If a substation site is physically small, like 100’ x 100’, it may not be possible, even with close ground grid spacing, to achieve the desirable amount of copper in the ground. Some of the suggestions and preferences noted in the step-by-step guidelines are reflective of years of design and operational experience with substations. Once the overall design parameters are addressed, the practical design is to be based upon IEEE 80-2000. The method in IEEE 80 is an iterative “trial and error” method but an acceptable solution can usually be achieved with just a couple of iterations. It should be noted that this design approach leads to a somewhat conservative design (more copper in the ground than may be necessary). The reasonable trade-off seems to be possibly spend a little more for copper in the ground (and purposely accept the improved ground grid design safety factor), rather than spending more money for expensive design software and test equipment (that soon will be outdated anyway). Procedure 1. Review the IEEE 80-2000 Standard entitled, “IEEE Guide for Safety in AC Substation Grounding.” 2. Define the following design parameters: • Substation soil resistivity. Hire one of the current CU blanket contractors, Anderson Engineering (866-2741) or Palmerton and Parrish (831-3056), to perform soil resistivity testing if recent, site specific, soil resistivity information does not exist. • Substation area and geometry • Available fault current at substation – to be obtained from Planning Engineer • Expected duration of fault 3. Confirm the use of certain design parameters and preferences including: • Presumption of the use of buried 4/0 bare copper ground conductor at 18” depth • Presumption of the use of 5/8” x 10’ copperclad ground rods • Presumption of the use of exothermic welds for all underground conductor connections • Presumption of the use of a 6” layer of coarse crushed rock surfacing (washed, with no fines) over the entire substation, and 3’ outside of the substation fence. • Typical spacing for the underground copper conductors should be on an approximate 20’ x 20’ grid pattern. • Ground rods should be installed periodically but particularly near major pieces of substation equipment like transformers, switchgear, and breakers. • A safety rule-of-thumb is to install a 4/0 ground conductor about 3’ outside of the substation perimeter fence and do a careful ground design at all gates and fence corners. • Another safety rule-of-thumb is to ground the fence posts, fence fabric, and strands of top barbed wire at every other post – so typically about every 20’. A rigorous approach to galvanic corrosion indicates that tinned 2/0 copper conductor and tinned connectors be used for galvanized chain link fence grounding 4. Prepare an AutoCad drawing with the proposed substation ground grid drawn to scale. Reference a previously designed, modern, CU substation, like Summit substation, for an example substation ground grid layout. 5. The ground grid design shall then used to develop a detailed ground grid layout drawing and bill-of-material list complete with item numbers, descriptions, manufacturer and catalog number. Reference the following Standards in the City Utilities’ Substation Standards Manual: A-GRD-1, Fence and Switch Platform, Grounding Details, A-GRD-2, Grounding Legend and Notes, and A-GRD-3, Grounding Plan and Sections, Bill of Material List. An example from Summit Substation may also be referenced in the master files. 6. Using the Excel spreadsheet software tool from Commonwealth Associates, Exhibit 1, located on the J:\Review/IEEE drive, confirm the proposed substation ground grid design. Several “trial and error” iterations, with differing substation ground grid geometry, may be needed to achieve an acceptable solution. See example printout attached. 7. The completed documents should be placed in the corresponding substation correspondence file for future reference. The AutoCad substation ground grid drawing file should reside in the J: directory under the proper substation name. End of Procedure Attachment: Exhibit 1, Ground Grid Calculations
5 | 2009-06-09 15:22 | The main disadvantage of IEEE 80 is, calculation performs for entire site but using of software gives us this opportunity to localize our design and we can save $$$$ dollars in this way. Formula in Std 80 also is based on 2 layer soil that is not adequate for big sites. I believe that we need major review on whole standard to be able to cover recent and future very high fault current values and also optimize our design
6 | 2009-06-09 17:57 | More information on methodology for stone testing. More information on use of deep wells to reduce grid resistance. The guys who worked on the latest revision did an outstanding job !
7 | 2009-06-10 13:25 | We're OK with the standard as written.
8 | 2009-06-10 14:33 | More practical case studies
9 | 2009-06-16 00:20 | Unsure
10 | 2009-06-17 13:57 | Perhaps better Split factor Curves or recommendation for other analysis which takes into account circulating currents for auto-transformers; currently am using CDEGS FCDIST to determine Split Factor but is very time consuming and requires information from utilities regarding 3I0 fault current analysis, line geometry, phase and neutral/shield wire data, line distances, and typical structure separation. Also need a specified test procedure for determining resistivity of wetted crushed rock; IEEE Transaction Paper in Vol. 7 No. 1, Jan. 1992 regarding "Measurement of Substation Rock Resistivity" presents a possible method but ASTM G 187, ASTM G 57, and AASHTO T 288-91 (2004) do not provide specific testing procedures for determining wetted crushed rock resistivity with egard to actual installed conditions; do not want to test the crushed rock after it has been pulverized for labratory testing methods.
11 | 2009-06-17 15:56 | There should have one section introduce the routine test approaches of the substation grounding.
12 | 2009-06-18 12:26 | shorten it or provide a supplement that is more "cook book" approach with more difinitive guidance
13 | 2009-06-19 13:41 | More discussion on probabilistic methods for earthing design rather than determinisitic. Clarification on why IEC curves differ so much from IEEE curves and hence drive some standardization across the industry. More clarification on re-enforced concrete mesh bonding - i.e. the benfits and drawbacks. Lots of other things that i can't think of now!
14 | 2009-06-23 09:30 | adding examples explanding on Transfer voltage Elaborating in mitigation methods Specifically metioned primary protection time as a recommended fault clearing time Include the risk based earthing design
15 | 2009-06-29 18:55 | The application and selection of commercial programs for station ground grid design.
16 | 2009-06-30 01:03 | allowable step voltage calculation fomular is to be modified to allow the body resisitance reduction of person standing on the ground with two feet
17 | 2009-07-02 21:06 | Cannot think of anything.
18 | 2009-07-10 14:14 | Clause for conductor sizing factors, please clarify temperatures for selection of joints (exothermic, brazing compression etc). Please clarify the sections on how to choose Shock duration time and fault duration time. Add an Index, like the version of IEEE 80-1986.
19 | 2009-07-13 18:38 | Additional discussion of grounding rebar in concrete.
20 | 2009-08-10 20:01 | Info about typical resistivities for more materials that could be used in calculations. It's often hard to find values for different types of rock. A treatment of concrete and how to treat it as a surface layer.

## Part 8_Question 2
Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices | Survey On Power System Grounding Design Practices
Part 8: Std 80 and Std 837 improvement suggestions.
Please tell us what can be added to the Std 837 that would complement your efforts. | Please tell us what can be added to the Std 837 that would complement your efforts. | Please tell us what can be added to the Std 837 that would complement your efforts.
Answer Options | Answer Options | Response Count
7
answered question | 7 | 7
skipped question | 98 | 98
Number | Response Date | Response Text
1 | 2009-06-09 05:32 | galvanic reaction of different materials. Cathodic proteciot for the below grade ground grid
2 | 2009-06-09 17:57 | Nothing to suggest.
3 | 2009-06-10 13:25 | We're OK with the standard as written.
4 | 2009-06-16 00:20 | Unsure
5 | 2009-06-18 12:26 | address above ground connections, address specific conductor to rod connections, address doubled or triple conductors in same connection
6 | 2009-06-29 18:55 | Fine-tune the test methods.
7 | 2009-07-02 21:06 | I don't think we have used this standard yet.