Lane Garrett, Chairman, opened the meeting with introductions.  There were 19 members and 15 guests present at this meeting.

- Obligatory Statement - Lane presented the obligatory slides from IEEE regarding patents in standards and inappropriate topics for working group meetings.

- Minutes/Agenda - The San Francisco 2008 working group meeting minutes and agenda of the Nashville 2008 meeting, were approved. (Kelley, Story)

- Review of the Assignments

| SECTION NUMBER | LEAD PERSON |
| --- | --- |
| 1-3 | Hanna Abdallah |
| 4 | Allan Love |
| 5 | Keith Wallace |
| 6 | F red Randolph |
| 7 | Keith Wallace |
| 8 | Alfred Flojo |
| Annex A | Keith Wallace |
| Annex B | Hanna Abdallah |
| Annex X | Phil Atwater |

- Hanna Abdallah – Did not find any problems with the sections. No progress on Annex B.

- Alan Love – Recommended that typical fault clearing times published in Table 1, of the current standard should be revised. The recommended change – for 230V from 3-8 to 2-8

- Keith Wallace – Submitted changes on section 7 and Annex A (Included in the first draft), no progress on section 5.

- Fred Randolph – Reviewed his comments with the working group in San Francisco.  (Included in the first draft).

- Alfred Flojo – Provided summary of section 8 changes in San Francisco. The changes were reviewed with the WG. (Included in the first draft)

- Phil Atwater – Submitted first draft of Annex X. The Annex X was reviewed by Lane and Shashi. (Included in the first draft).

- Review of the Annex X - Phil was not able to attend the meeting. Lane reviewed the Annex for the group. Sashi presented a model of the safety jumpers in WinIGS for comparison. (Annex X is included in the first draft).

- Assignments -  for the January Atlanta meeting Sashi to evaluated the same model  using calculated impedances with Formula 1. of the Annex X. Marcia will do the same simulation in CDEGS

- ASTM F 855 EMF test update – the ASTM F 855 working group agreed on the new EF test currents that will also be adopted in the IEEE Standard 1246. Refer to the following:

| Table 2 - Ultimate Assembly Rating for High X/R Ratio Applications |
| --- |
| High Asymmetrical Test Requirements |
|  |  | Rating | X/R = 30 |  |  |
| Grade | Size | Rated Current (kA) | 1st Cycle Current Peak (kA) | Last Cycle Current Peak (kA) | Test Duration (cycles) |
|  |  |  | X 2.69 |  |  |
| 1H | #2 | 15 | 41 | 23 | 15 |
| 2H | 1/0 | 25 | 65 | 37 | 15 |
| 3H | 2/0 | 31 | 84 | 46 | 15 |
| 4H | 3/0 | 39 | 105 | 58 | 15 |
| 5H | 4/0 | 47 | 126 | 70 | 15 |
| 6H | 250 MCM | 55 | 148 | 82 | 15 |
| 7H | 350 MCM | 68 | 183 | 101 | 15 |

| Notes: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | The above current values are based on electromechanical test values |
| 2 | Assemblies that have been subjected to these shall not be re-used |
| 3 | For use with currents exceeding 20% asymmetry factor |
| 4 | See Appendix X4.7.2 for additional information |
| 5 | Alternate testing circuits are available for laboratories that cannot achieve the above requirements. See Appendix X4 for details |

The date and time of the winter 2009 Atlanta meeting will be announced.  Please submit all assignments two weeks prior to the Atlanta meeting to the secretary at mhavelka@ieee.org

Respectfully submitted by

Martin Havelka

Secretary, WG D4

# Attendance

| NAME | ROLE | P* | CONTACT INFORMATIOM |
| --- | --- | --- | --- |
| Abdallah, Hanna | member | X | Arizona Public Service Co, Phoenix, AZ, hannaEssa.Abdulah@aps.com |
| Arnot Stan | member | X | Toronto, ON, Canada, santro@sympatico.ca |
| Atwater Philip | member | - | Bureau of Reclamation, Denver, CO, patwater@do.usbr.gov |
| Barnes, Thomas | member | - | Allen & Hoshall, Inc. Nashville, TN, tbarnes@ge.com |
| Beske, Bryan | member | X | American Transmission Company, Madison, WI, bbeske@atcllc.com |
| Brown Steven | member | X | Memphis Light Gass & Water, Memphis, TN, stevendbrown@ieee.org |
| Cain James | member | X | Stanley Consultants, Inc., Phoenix, AZ, cainbrian@stanleygroup.org |
| Chadbourne Chris | member | - | FCI USA, Inc., NH, chris.chatdbourne@fciconnect.com |
| Chan K.S. | member | - | Bechtel, Huston, TX, kschan@bechtel.com |
| Chandra Kouskik | member | X | Bechtel, Huston, TX, kchanda@bechtel.com |
| Chisholm William | member | - | Kinetriccs, Toronto, Canada, w.a.chisholm@ieee.org |
| Darkenwald Greg | member | - | NorthWestern Energy, Butte, MT, gregd@northwestern.com |
| Denbrock Frank | member | - | D&A Consulting Engineers, Jackson, MI, denbrock@prodigy.net |
| Dick Eugene | member | - | Electric Power Diagnostics, Toronto, Canada, epdick@ieee.org |
| Eblen Marcia | member | X | Pacific Gas & Electric, San Ramon, CA, mls2@pge.com |
| Engmann, Gary | member | X | Burns & McDonnell, Leadwood, KS, g.engmann@ieee.org |
| Garrett, Lane | chair | X | Alabama Power Company, Birmingham, AL, dlgarret@southernco.com |
| Greenfield, Steve | member | X | ERICO, West Palm Beach, FL, sgreenfield@erico.com |
| Havelka, Martin | secretar | X | ERICO, Solon, OH. mhavelka@erico.com |
| Kahanek William | member | - | Bluerbonnet Electric Coop, Giddings, TX, bil.kahanek@bluebonnetelectric.coop |
| Keil Rich | member | X | Commonwealth Associates Inc., Dayton, OH, rpkeil@cai-eng.com |
| Kelley, Dave | member | X | Salt River Project, Phoenix, AR, dave.kelley@srpnet.com |
| Kollar Allen | member | - | FirstEnergy Corp., Akron, OH, kollara@firstenergycorp.com |
| Larid Donald | member | - | Southern California Edison, Rosemead, CA, Donald.Larid@sce.com |
| Love, Allen | member | X | Georgia Power Co., Forest Park, GA, alcove@southernco.com |
| Marryman Jeffrey | member | - | ABB Inc., Releigh, NC, Jeffrey.marryman@us.abb.com |
| Middlecamp Steven | member | - | Florida Power & Light Co., Juno B., FL, steven_c_middlecamp@fpl.com |
| Nowell, R. S. (Bob) | member | X | Georgia Power Company, Atlanta, GA, rsnowell@southernco.com |
| O’Donnell, Edward | member | - | Baltimore Gass & Electric, Baltimore, MD, edward.j.odonnell@bge.com |
| Palmer-Buckle, Peter | member | - | Burns & McDonnell, Kennesaw, GA, oko@ieee.org |
| Patel Shashi | member | X | NEETRAC, Forest Park, GA, patel@ee.gatech.edu |
| Perkins Samuel | member | - | Bonneville Power Admin., Vancouver, Canada, scperkins@bpa.gov |
| Polak Janusz | member | - | Hydro One, Toronto, Canada, janusz.polka@hydroone.com |
| Rockwell Bruce | member | - | American Transmission Company, Boonton, NJ, brockwell@99eatco.com |
| Sheh Will | member | X | TectoWeld Inc., Torrance, CA, wshash@atitec.com |
| Stidham Curt | member | - | Harger Lightning & Grounding, Grayslake IL, cstidham@harger.com |
| Story Brian | member | X | Entergy, Kenner, LA, bstory@entergy.com |
| Wallace Keith | member | X | Alabama Power Co., Birmingham, Al, kawallac@southernco.com |
| Watkins Diane | member | - | David Evans& Associates, Phonix, AZ, dwarkins@deainc.com |
| Sharifnia, Hamid | guest | X | Pacific Corp, Portland, OR, hamids@ieee.org |
| Boling Dale | guest | X | ERICO International, Inc., Solon, Oh, dboling@erico.com |
| Herman Voch | guest | X | Siemens, herman.voch@siemens.com |
| Giang Tran | guest | X | Entergy, gtran@entergy.com |
| Bernards Louis | guest | X | Burns & McDonnell, Leadwood, KS, g.engmann@ieee.org |
| Haahr Charles | guest | X | Sega Inc., Olathe, KS, chaahr@segaind.com |
| Baroc, Radoslav | guest | X | GE, Oakbrook Terrace, IL, radoslav.baroc@ge.com |
| Noori Mike | guest | X | Custom Engineering Solutions, mike@cengs.comKing |
| King, Kyle | guest | X | K+R Consulting, Lenox, MA, kking@kandrllc.com |
| Evans Jim | guest | X | PES, j.evans@pes.com |
| Farmer Brian | guest | X | PG&E, bkfi@pge.com |
| Bashirian Hassein | guest | X | Georgia Power Company, Atlanta, GA, hbashiri@southernco.com |
| Smith Dough | guest | X | SEFCOR, Inc., Griffin, GA, doughsmith@ieee.org |
| White, Ken | guest | X | Georgia Transmission Corp., Tucker, GA, ken.white@ieee.org |
| Clelland Randy | guest | X | BC Hydro, Burnably, BC, randy.clelland@bchydro.com |