## Sheet1
<<<< question count
2017-01-10
IEEE WORKING GROUP E-6 GROUND TESTING SURVEY - DRAFT
Key points to consider when developing each section:
A. Does the question relate directly to ground testing or is it straying into ground grid design?
B. Does the question translate well into survey software? (Steve Greenfield to provide sage advice!)
C. Can the data obtained from the survey be compiled in a meaningful manner? (This may mean simplifying some questions into a yes or no answer and keeping the number of text responses to a minimum)
D. Can the overall questionnaire be completed in 20 minutes? (different time?)
|  | 1 | Introduction and Purpose of the Survey IEEE Working Group E-6 in the Substations Committee of the Power & Energy Society is presently working on the next revision of IEEE Std 81, “Guide for Measuring Earth Resistivity, Ground Impedance and Surface Potentials of a Grounding System”. The working group has decided to conduct a survey as part of the revision process to:
1 |  | 1.1 | Determine the methods and practices currently applied worldwide to measure the electrical characteristics of grounding systems and soil. | no answers needed for these line items
2 |  | 1.2 | Understand how IEEE Std 81 is applied
3 |  | 1.3 | Identify areas of IEEE Std 81 that can be improved.
4 |  | 1.4 | Use the information gathered in the survey to update and enhance the next edition of IEEE Std 81.
If you have any questions while taking this survey, or comments when you are finished, please contact XXXX XXXX at “xxxx@xxxx.com.
|  | 2 | Professional Affiliation
Please tell us about your professional affiliation:
5 | 1 |  | Name:
6 | 2 |  | Company:
7 | 3 |  | Company type: Place "X" In Box | Utility | Independent Power Producer | Industrial | Government | Consultant | Contractor | Academic
Add Asset types here
8 | 4 |  | Title:
9 | 5 |  | Address:
10 | 6 |  | City/Town:
11 | 7 |  | State or Provence:
12 | 8 |  | ZIP/Postal Code:
13 | 9 |  | Country:
14 | 10 |  | Email Address:
15 | 11 |  | Phone Number:
|  |  | How aware/familiar are you of Std 81? | No idea | heard of it | somewhat | used it before | folllow it always
|  | 3 | Current injection testing (Ehsan Azordegan)
16 | 12 | 3.1a | Do you measure the ground impedance using any of the methods described in IEEE 81? | YES | NO
Place "X" In Box
|  |  |  | if yes do 3.1b | If no. Goto 3.1C
17 | 13 | 3.1b | If the answer to previous question is ‘Yes' what method(s) are you using? List all test methods used. | Two-point method | Three-point method | Staged fault tests | Fall-of-potential method | Resistance measurements by clamp-on or stakeless method | Resistance measurements by FOP/clamp-on method | Ground impedance measurement by computer-based grounding multimeter
Place "X" In Box
| 14 | 3.1c | Please provide information of other method used | enter answer in memo/text field
18 | 15 | 3.2 | How far away do you place your current probe? | 3 - 5 times the largest dimension of the ground electrode under test. | 5 - 7 times the largest dimension of the ground electrode under test. | More than 7 times the largest dimension of the ground electrode under test. | The current probe location is not a function of station dimension
Place "X" In Box
19 | 16 | 3.3 | Do you run the potential probes in the same direction as the current probe? | Always | Sometimes | Never
Place "X" In Box
20 | 17 | 3.4 | If using a locally run lead as a current injection circuit do you repeat tests with a different current probe location? | YES | NO
Place "X" In Box
21 | 18 | 3.5a | Which methods do you use for interpreting the fall of potential test results to determine a ‘test’ impedance? | 62% rule | Flattest part of curve | Slope method | Using IEEE 81 multilayer soil graphs to find the proper potential probe position. | Using software to adjust for galvanic coupling between P2, C2 and the grounding system under test. | Using software to correct for mutual coupling between conductors (wherever injection current flows) and the ‘fall of potential’ test lead - when impedances are low and leads are long. | Use remote injection location, with power line used as injection circuit, to remove mutual ground resistance error. | Using software to adjust for external impedance parallel to grid resistance
Place "X" In Box
| 19 | 3.5b | Other Comments here | enter answer in memo/text field
22 | 20 | 3.6 | Do you perform the Fall of Potential test on grounding electrodes with external connections (such as shield wires, distribution neutrals)? | YES | NO
Place "X" In Box
23 | 21 | 3.7 | Do you correct for system impedance variations between the current injection frequency and power system frequency? | YES | NO
Place "X" In Box
24 | 22 | 3.8 | Do you use a power line to inject test current into a ‘remote’ station grid? | Whenever Possible | NO
Place "X" In Box
25 | 23 | 3.9 | Do you compare the impedance test results to expected results available from the design? | YES | NO
Place "X" In Box
#REF! | 24 | 3.1 | As a part of the test result ‘interpretation’ process do you consider how the various ‘real life’ fault locations will create different inductive and conductive currents flows than those present in the injection configuration being simulated by the test arrangement? | YES | NO
Place "X" In Box
#REF! | 25 | 3.11a | Do you measure step and touch potentials as part of the ground impedance tests? | YES | NO
Place "X" In Box
if yes do 3.11b
#REF! | 26 | 3.11b | If you answered ‘Yes' to the previous question, what type of step and touch potentials do you measure? | Step voltage inside the station | Step voltage outside the station on native soil | Structure touch voltage | Mesh touch voltage | Fence touch voltage | Gate touch voltage | Transferred touch voltages outside station
Place "X" In Box
#REF! | 27 | 3.12 | What method(s) do you use for measuring the step and touch potentials? | Use two probes and measure open circuit impedance across a high impedance voltmeter. | Measuring two potentials relative to the station ground and subtracting the two.
Place "X" In Box
#REF! | 28 | 3.13 | During step and touch measurements, do you add a shunt body resistance in the measurement (say 1000 ohm)? | Always yes | Only if open circuit measurement gives a high value | NO
Place "X" In Box
#REF! | 29 | 3.14 | How do you account for the effect of surface moisture when taking touch voltage measurements? | The effect of moisture is simulated by wetting surface under the ‘foot’ electrode | Moisture is not considered during measurement
Place "X" In Box
#REF! | 30 | 3.15a | Do the measured GPR, Step and Touch potentials get corrected to allow for changes in soil conditions in a different season? (eg top soil drying out in summer, frozen topsoil in winter) | YES | NO
Place "X" In Box
if yes do 3.15b
#REF! | 31 | 3.15b | If you answered ‘Yes' to the previous question, how to you model the variations in soil structure? | 3rd party software to estimate the winter soil model | Multiply the top layer soil by a conservative factor to represent the top frozen soil layer | Performing measurements during winter or summer time
Place "X" In Box
#REF! | 32 | 3.16a | Do you test large interconnected grounding systems (eg interconnected with a large multi grounded neutral in a built up area, a power station, extensive industrial complex or mining installation)? | YES | NO
Place "X" In Box
if yes do 3.16b
#REF! | 33 | 3.16b | If so, how do you configure the test and interpret the results? Comment: | enter answer in memo/text field
#REF! | 34 | 3.17 | Do you think developing guidelines regarding how to test large interconnected grounding systems using current injection would be useful? | YES | NO
Place "X" In Box
#REF! | 35 | 3.18 | How helpful do you find IEEE Std 81 with regard to current injection testing? | Extremely | Very | Somewhat | Of Little Importance
Place "X" In Box
#REF! | 36 | 3.19 | Are there any issues or topics related to current injection testing you'd like to see IEEE Std 81 address better? | enter answer in memo/text field
|  | 4 | Soil resistivity testing (Bill Carman)
|  | 4.1 | Do you perform soil resistivity measurements when designing a ground electrode system? Check all that apply. | YES Place "X" In Box |  |  |  |  | NO
|  |  | Asset Type: Let's refine these catagories below . | Driven ground (3-pin method) | Equally spaced Wenner (4-pin method) | Unequally spaced Schlumberger (4-pin method) | Inductive method | Other
#REF! | 37 | 4.1a | Laboratory information from soil core samples
#REF! | 38 | 4.1b | Power plant (Renewable)
#REF! | 39 | 4.1c | Transmission substation (Over 69 kV)
#REF! | 40 | 4.1d | Distribution substation (69 kV & under)
#REF! | 41 | 4.1e | Transmission Structures
#REF! | 42 | 4.1f | Commercial & industrial buildings
#REF! | 43 | 4.1g | Residential buildings
#REF! | 44 | 4.1h | Other
|  | 4.2 | When undertaking a soil resistivity test do you use any of the following procedures?
|  |  | Procedure: . | YES Place "X" In Box | NO
#REF! | 45 | 4.2a | Check pin spacing with tape measure
#REF! | 46 | 4.2b | Calculate apparent resistivity and plot results as tests are performed
#REF! | 47 | 4.2c | Measure pin resistances
#REF! | 48 | 4.2d | Check for conductive paths (i.e. pipelines, fences, rails, overhead conductors etc.) above and below ground level
#REF! | 49 | 4.2e | Use multiple pins when resistance too high
#REF! | 50 | 4.2f | Use water to help reduce pin resistance
| 51 | 4.3 | How do you determine the minimum and maximum pin spacing? | enter answer in memo/text field
#REF! | 52 | 4.4 | How do you achieve wide pin spacing when undertaking a Wenner test in a built up area? | enter answer in memo/text field
|  | 4.5 | How do you interpret test results to determine soil models for use in designing ground grids?
|  |  | Procedure: . | YES Place "X" In Box | NO
#REF! | 53 | 4.5a | Use exact results from one selected traverse (orientation, direction)
#REF! | 54 | 4.5b | Base model on average of readings for like pin spacing
#REF! | 55 | 4.5c | Determine a soil model for each traverse
#REF! | 56 | 4.5d | Other Comments here | enter answer in memo/text field
|  | 4.6 | What additional information do you consider in interpreting soil resistivity values?
|  |  | Information Type: . | YES Place "X" In Box | NO
#REF! | 57 | 4.6a | Soil type - from site geological assessments
#REF! | 58 | 4.6b | Table of standard soil resistivity values based on soil type
#REF! | 59 | 4.6c | Geological plans
#REF! | 60 | 4.6d | Seasonal effects
#REF! | 61 | 4.6e | Recent rainfall
#REF! | 62 | 4.6f | Laboratory information from soil core samples
#REF! | 63 | 4.6g | Other
| 64 | 4.6h | Explain how you have used the items you marked "Yes" when deciding upon a soil model(s) to use when designing a grounding system | enter answer in memo/text field
#REF! | 65 | 4.7 | How helpful do you find IEEE Std 81 with regard to soil resistivity testing? | Extremely | Very | Somewhat | Of Little Importance
Place "X" In Box
#REF! | 66 | 4.8 | Are there any issues or topics related to soil resistivity testing you'd like to see IEEE Std 81 address better? | enter answer in memo/text field
|  | 5 | Integrity Testing (Steve Greenfield)
|  |  | New grounding Systems: | depending on how the survey system works, New and Existing verbage may need to be worked into the text of each question OR those sections may be the number question with each question treated as a subquestion (ex: 5.1 New grounding Systems will have 5.1a and 5.1b.
#REF! | 67 | 5.1 | Do you undertake any form of integrity testing of new grounding systems? | Always | Sometimes | Never
Place "X" In Box
#REF! | 68 | 5.2 | How important do you think integrity testing is during the commmisioning of a new substation? | Essential | Very Important | Somewhat Important | Of Little Importance
Place "X" In Box
Existing grounding Systems:
#REF! | 69 | 5.3 | How often do you perform integrity testing on existing grounding systems? | 1-3 years | 4-6 years | >6 years | Never | After An Incident | Associated with a modification project | After a lightning event
Place "X" In Box
#REF! | 70 | 5.4 | How important do you think periodic integrity testing is, during the life of a substation? | Essential | Very Important | Somewhat Important | Of Little Importance
Place "X" In Box
#REF! | 71 | 5.5 | What maintenance procedures are applicable to grounding elements associated with particular assets and when? Eg portable ground connection points, gate braids, paths actively involved in managing load conditions such as transformer neutral, CVT, single point bonded cable grid connections. | enter answer in memo/text field
#REF! | 72 | 5.6a | If the integrity of the grounding system is compromised, what were the usual causes? | Dig-ins or mechanical damage | Corrosion | Faulty connector installation | Lightning | Short circuit | Copper theft
Place "X" In Box
| 73 | 5.6b | Enter other or unknown here
General:
#REF! | 74 | 5.7a | What method of ground electrode system integrity testing do you use? | High Current 10-300A 60 Hz AC | Resistance Between Risers 25-30A 60Hz AC | Computer Based Multimeter | dc 4-point resistance measurement
Place "X" In Box
| 75 | 5.7b | Other (please specify) | enter answer in memo/text field
| 76 | 5.7c | Which instrument is used to perform ground integrity testing? | enter answer in memo/text field
#REF! | 77 | 5.8 | How helpful do you find IEEE Std 81 with regard to ground grid integrity testing? | Extremely | Very | Somewhat | Of Little Importance
Place "X" In Box
#REF! | 78 | 5.9 | Are there any issues or topics related to ground grid integrity testing you'd like to see IEEE Std 81 address better? | enter answer in memo/text field
|  | 6 | Crushed Aggregate Testing (Dennis DeCosta/Bryan Beske)
#REF! | 79 | 6.1 | Do you use surface materials to limit body current due to step and touch voltages? | YES | NO
Place "X" In Box
#REF! | 80 | 6.2a | Do you perform electrical resistivity testing on the surface materials to verify its resistivity? | YES | NO
Place "X" In Box
if no do 6.2b
#REF! | 81 | 6.2b | If the answer to 6.2a was no, what value resistivity do you assume? | <1,000 Ω-m | 1,000 - 2,999 Ω-m | 3,000 - 5,999 Ω-m | 6,000 - 10,000 Ω-m | >10,000 Ω-m
Place "X" In Box
#REF! | 82 | 6.3 | If you perform resistivity measurements on crushed rock or other surfacing material, what test method do you primarily use? | enter answer in memo/text field
#REF! | 83 | 6.4 | When you perform resistivity measurements on crushed rock, do you test the rock under wet and/or dry conditions? | DRY | WET | BOTH
Place "X" In Box
#REF! | 84 | 6.5 | What variability in resistivity are you experiencing in aggregate supply? | enter answer in memo/text field
#REF! | 85 | 6.6 | Is the variability related to different source quarries, or from a single quarry? | different sources quarries | single quarry
Place "X" In Box
#REF! | 86 | 6.7 | How helpful do you find IEEE Std 81 with regard to crushed aggregate testing? | Extremely | Very | Somewhat | Of Little Importance
Place "X" In Box
#REF! | 87 | 6.8 | Are there any issues or topics related to crushed aggregate testing you'd like to see IEEE Std 81 address better? | enter answer in memo/text field
|  | 7 | Transient impedance testing (Dennis DeCosta)
#REF! | 88 | 7.1 | Do you measure the impedance of a ground system under conditions simulating a lightning stroke to confirm that the grounding system provides a low ground impedance and not just a low resistance? | YES | NO
Place "X" In Box
#REF! | 89 | 7.2 | If you perform transient impedance testing, please describe the test method that you use. | enter answer in memo/text field
#REF! | 90 | 7.3 | How helpful do you find IEEE Std 81 with regard to transient impedance testing? | Extremely | Very | Somewhat | Of Little Importance
Place "X" In Box
#REF! | 91 | 7.4 | Are there any issues or topics related to transient impedance testing you'd like to see IEEE Std 81 address better? | enter answer in memo/text field
|  | 8 | Testing for Interaction with other systems (Bill Carman)
#REF! |  | 8.1 | During load and fault conditions, power systems may affect metallic third party assets. Which thrid party assets do you consider and how do you evaluate each type of asset? (check all applicable) | Telephone/communication lines and equipment interface points | Pipelines and associated plant such as regulating stations and operating points | Mining plant - conveyors and cables | Railway infrastructure - tracks and signalling | Other (specify)
| 92 | 8.1a | Computer simulation
| 93 | 8.1b | Testing
| 94 | 8.1c | Not considered
if check in 8.1b (any column, do 8.2, otherwise skip to 8.3
#REF! | 95 | 8.2 | If you perform interference testing, please explain your test method | Telephone/communication lines and equipment interface points | Pipelines and associated plant such as regulating stations and operating points | Mining plant - conveyors and cables | Railway infrastructure - tracks and signalling
|  |  |  | enter answer in memo/text field | enter answer in memo/text field | enter answer in memo/text field | enter answer in memo/text field
#REF! | 96 | 8.3 | How helpful do you find IEEE Std 81 with regard to interacting with other utilities? Extremely-very-somewhat- of little importance - not applicable (dropdown box with blank)
Place "X" In Box
#REF! | 97 | 8.4 | Are there any issues or topics related to interacting with other utilities you'd like to see IEEE Std 81 address better? | enter answer in memo/text field
|  | 9 | Other
#REF! | 98 | 9.1 | Please provide any observations or suggestions for consideration in the next edition of IEEE Std 81. | enter answer in memo/text field
#REF! | 99 | 9.2 | Would you be prepared to assist the working group by providing practical examples, technical materials, answering questions, etc.? | YES | NO
Place "X" In Box

## Sheet3 (hidden)
Column1 | #REF! | Current injection testing (Ehsan Azordegan) | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14 | Column15 | Column16 | Column17
doc | #REF! | In your opinion, regarding testing ground electrodes, what topics/methods can be added into the next revision of IEEE 81? | Column2: enter answer in memo/text field
faults | #VALUE! | How do you relate test results to results expected under real fault conditions?
faults | #VALUE! | Do you use current split measurements to enable scaling and modeling to be done to accommodate the contribution of alternate fault sources and paths.
Place "X" In Box
faults | 0.1 | Do you consider a range of alternative ground fault scenarios in order to determine equipment rating requirements and safety compliance? If so which scenarios – primary within the substation, primary upstream of the substation, secondary within the substation, and secondary downstream of the substation?
faults | 0.01 | To calculate the maximum injected fault current to the ground electrode, what types of fault scenarios do you consider: | Column2: Single Line to ground faults; Column3: Double Line to ground Faults; Column4: Three phase to ground faults
faults | 0.02 | To calculate the maximum injected fault current to the ground electrode, what fault locations do you consider: | Column2: Primary within the substation; Column3: Primary upstream the substation; Column4: Secondary within the substation; Column5: Secondary outside the substation
faults | 0.02 | Do you think developing examples on how to calculate the portion of the maximum fault current that will be injected into the grounding system (considering different transformer configurations and different types of fault) would be useful? (rate it from 1 to 10) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
fop | 0.12 | Do you use the FOP test result directly to provide a real answer? If so what?
fop | 0.13 | If you are using the Fall of Potential test method, how far do you place your current probe? | Primary within the substation 1: 3 - 5 times the largest dimension of the ground electrode under test.; Primary upstream the substation 2: 5 - 7 times the largest dimension of the ground electrode under test.; Secondary within the substation 3: More than 7 times the largest dimension of the ground electrode under test.; Secondary outside the substation 4: The current probe location is not a function of station dimension
fop | 0.14 | If you are using the Fall of Potential test method, do you run the potential probes in the same direction of current probe? | Primary within the substation 1: Always; Primary upstream the substation 2: Sometimes; Secondary within the substation 3: Never
fop | 0.15 | When interpreting the Fall of potential test results, Do you assume a uniform soil? | Primary within the substation 1: YES; Primary upstream the substation 2: NO
general b | 0.16 | Would guidelines regarding how to undertake practicalities of injection testing be useful?
general b | 0.17 | Do you use checklists when planning, undertaking and analyzing current injection test results? Would checklists be helpful for engineers and technicians?
Place "X" In Box
general t | 0.01 | Do you measure the ground impedance using any of the methods described in IEEE 81? | Primary within the substation 1: YES; Primary upstream the substation 2: NO
general t | 0.01 | If the answer to previous question is "YES" what method are you using? | Two-point method | Three-point method | Staged fault tests | Fall-of-potential method | Resistance measurements by clamp-on or stakeless method | Resistance measurements by FOP/clamp-on method | Ground impedance measurement by computer-based grounding multimeter | Other (please specify)
gpr | 3.1 | Are there any criteria commonly used as targets for maximum grid resistance or GPR? If so, what was the purpose of the target and was there any supporting analysis available?
gpr, fault | 3.2 | It has been suggested that measuring standing 60Hz GPR is a good indicator of likely problems under fault conditions. If so what values are considered unacceptable, and what actions are taken? Is there any supporting analysis available?
Place "X" In Box
interpet | 3.21 | Interpretation when potential and currents probes are not in line? | Primary within the substation 1: 62 % rule; Primary upstream the substation 2: Flattest part of curve; Secondary within the substation 3: Slope method; Secondary outside the substation 4: Using IEEE 81 multilayer soil graphs to find the proper potential probe position.; Secondary outside the substation 5: Using software to adjust for galvanic coupling between P2, C2 and the grid
interpet | 3.22 | Interpretation when there are external interconnections? | Primary within the substation 1: 62 % rule; Primary upstream the substation 2: Flattest part of curve; Secondary within the substation 3: Slope method; Secondary outside the substation 4: Using IEEE 81 multilayer soil graphs to find the proper potential probe position.; Secondary outside the substation 5: Using software to adjust for external impedance parallel to grid resistance
logistics | 3.1 | What happens when testing in a built up area? How do you configure the test in a built up area, and interpret the results?
Place "X" In Box
logistics | 0.01 | What happens when testing in a built up area? How do you configure the test in a built up area, and interpret the results? | Primary within the substation 1: enter answer in memo/text field
process | 0.02 | Do you perform the Fall of Potential test on grounding electrodes with external connections (such as skywires, distribution neutrals, etc.)? | Primary within the substation 1: YES; Primary upstream the substation 2: NO
process | 0.03 | Do you correct for mutual coupling between test leads when impedances are low and leads are long? | Primary within the substation 1: YES; Primary upstream the substation 2: NO
Place "X" In Box
process | 0.04 | Do you repeat tests with a different current probe location? | Primary within the substation 1: YES; Primary upstream the substation 2: NO
Place "X" In Box
process | 0.05 | If you answered "NO", what test method do you use for measuring the impedance of interconnected grounding electrodes? | Primary within the substation 1: Current Injection; Primary upstream the substation 2: Other ( please specify)
process | 0.06 | Do you measure step and touch potentials as part of the ground impedance tests? | Primary within the substation 1: YES; Primary upstream the substation 2: NO
Place "X" In Box
process | 0.07 | If you answered "Yes" to the previous question, what type of step and touch potentials do you measure? | Step voltage inside the station | Step voltage outside the station on native soil | Structure touch voltage | Mesh touch voltage | Fence touch voltage | Gate touch voltage | Station transferred touch voltage | Remote transferred touch voltage
Place "X" In Box
process | 0.01 | What method do you use for measuring the step and touch potentials? | Primary within the substation 1: Use two probes and return difference to meter with a cable pair; Primary upstream the substation 2: Measuring two potentials relative to the station ground and subtracting the two; Secondary within the substation 3: Frequency selective hand held instruments to measure the potential difference
process | 0.02 | What method do you use for measuring touch potentials? | Primary within the substation 1: Use one probe and return potential to meter with a single conductor; Primary upstream the substation 2: Use one probe and return difference potential to nearby fence or structure with a cable pair; Secondary within the substation 3: Frequency selective hand held instruments to measure the potential difference
process | 0.03 | During step and touch measurements, do you add a shunt body resistance in the measurement (say 1000 ohm)? | Primary within the substation 1: YES; Primary upstream the substation 2: NO
Place "X" In Box
process | 0.04 | Do you report the estimated GPR, Step and Touch potentials for Winter conditions based on the impedance tests performed in the summer time? | Primary within the substation 1: YES; Primary upstream the substation 2: NO
process | 0.01 | If you answered "Yes" to the previous question, how to you model the winter soil structure? | Primary within the substation 1: 3rd party software to estimate the winter soil model; Primary upstream the substation 2: Multiply the top layer soil by a conservative factor to represent the top frozen soil layer; Secondary within the substation 3: Performing measurements during winter time
process | 0.02 | Do you think developing guidelines regarding how to test interconnected grounding systems using current injection would be useful? (rate it from 1 to 10) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
process | 0.02 | Do you think adding a section to address the effect of winter conditions on soil resistivity would be useful? (rate it from 1 to 10) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Place "X" In Box
process | 0.01 | Moisture can make a big difference (especially for large aggregate) to surface layer resistance, how do you account for moisture is your measurement? | 3rd party software to estimate the winter soil model 1 1: Moisture is not considered during measurement analysis; Multiply the top layer soil by a conservative factor to represent the top frozen soil layer 2 2: The effect of moisture is modelled
Place "X" In Box
tv, sv, r… | 0.1 | What are some of the practical ways that you use to measure touch and step voltage using probe and/or plate? Do you include any additional resistance in the measurement? If so when, and for what purpose? Moisture can make a big difference (especially for large aggregate) to surface layer resistance, and had already, how is the moisture effect ‘modeled’?
validate | 0.11 | Do you use software modelling to support the impedance measurement results obtained during the tests? | 3rd party software to estimate the winter soil model 1 1: YES; Multiply the top layer soil by a conservative factor to represent the top frozen soil layer 2 2: NO
Place "X" In Box
validate | 0.12 | Do you compare the impedance test results to expected results available from the design? | 3rd party software to estimate the winter soil model 1 1: YES; Multiply the top layer soil by a conservative factor to represent the top frozen soil layer 2 2: NO
Place "X" In Box
| 0.1 | 1.3 Do you use current injection testing using fall of potential and touch voltage measurements? | 3rd party software to estimate the winter soil model 1 1: YES; Multiply the top layer soil by a conservative factor to represent the top frozen soil layer 2 2: NO
Place "X" In Box
| 0.1 | Do you use Fall of Potential (FOP) testing in order to confirm a software model? What process is used to undertake this analysis?
| 0.01 | Which method do you use for interpreting the test results when the soil is close to uniform, the potential and current probes are in line and there are no external interconnections such as distribution neutrals or skywires? | 3rd party software to estimate the winter soil model 1 1: 62% rule; Multiply the top layer soil by a conservative factor to represent the top frozen soil layer 2 2: Flattest part of curve; Performing measurements during winter time 3 3: Slope method; Performing measurements during winter time 5 5: Using software to adjust for galvanic coupling between P2, C2 and the grid
| 0.02 | Interpretation when soil is not close to uniform? | 3rd party software to estimate the winter soil model 1 1: 62 % rule; Multiply the top layer soil by a conservative factor to represent the top frozen soil layer 2 2: Flattest part of curve; Performing measurements during winter time 3 3: Slope method; Performing measurements during winter time 4 4: Using IEEE 81 multilayer soil graphs to find the proper potential probe position.; Performing measurements during winter time 5 5: Using software to adjust for galvanic coupling between P2, C2 and the grid