Insulator Performance and Applications WG

July 22nd, 2008

Chair:  Allen Bernstorf

Attendance:   The meeting was convened at 8:00 a.m.  Thirty-five individuals were present.  A roster was routed for review.

Minutes:  The minutes of the last meeting were approved as submitted

Agenda:  The agenda for the current meeting was accepted.

Reports:  The following reports were made.

15.09.03.01: Task Force on Aging of Outdoor Insulator Dielectric Materials

Chair:  Dr. John Kuffel – Kinectrics

Dr. Kuffel expressed surprise that he was chair of this committee.  Organization will ensue.

| Planned Date | Summer 2008 | Winter 2009 | Summer 2009 | Winter 2010 | Summer 2010 |
| --- | --- | --- | --- | --- | --- |
| Task | Outline | First Draft/PAR | Final Draft | Submission | Review Resolved |
| Actual | Late |  |  |  |  |

15.09.03.02:  Task Force on Improving In-Service Contamination Performance

Chair:  David Shaffner

David Shaffner was unable to attend.  Mr. Burnham expressed concern  that the TF is not moving forward.  The work is somewhat delayed pending publication of the revision of the contamination paper (TPWRD-00575) which is still under review.  Dr. George Karady is the point man on the contamination paper.   Right now the paper exists in two parts.

| Planned Date | Winter 2007 | Summer 2007 | Winter 2008 | Summer 2008 |
| --- | --- | --- | --- | --- |
| Task | Rough Draft | Final Draft | Submission | Review Resolved |
| Actual | On Schedule | Late | Late |  |

15.09.03.03 – Task Force on Electric Field Modeling of Nonceramic Insulators

Chair:  Dr. Andrew Phillips

Dr. Phillips observed that the TF has made a great deal of progress since the last General Meeting.  A paper was published in April 2008 by the TF on Electric Fields and Composite Insulators.      The TF has dev eloped a generic model to allow techniques to be calibrated.  Lapp, MPS, NGK-Locke and Sediver are participating.  FEA doesn’t like working close to the surface.  Boundary element methods don’t seem to mind.   Results of all modelers correlate well.  Adding a corona ring causes a great deal of scatter in the data.  The TF is working on modeling a deadend insulator.  Current models are considering 138 kV.   At higher voltages, phase spacings increase so the problem gets simpler.

| Planned Date | Summer 2007 | Winter 2008 | Summer 2008 | Winter 2009 | Summer 2009 |
| --- | --- | --- | --- | --- | --- |
| Task | Outline | Rough Draft/PAR | Final Draft | Submission | Review Resolved |
| Actual | On Schedule | Late |  |  |  |

15.09.03.04:  Task Force on Bird Related Outages -

Chair: Dr. Raji Sundararajan

The PAR has been extended to 2009 for this paper.   The plan is to use IEEE 1264 as a guide and draft a paper.  The new standard will be IEEE 1651.  Right now it’s P1651/DA.  As a guide, it can be modified on a 5 year cycle.  Much of the guide has been drafted.  Some finishing work is underway.   The guide should be ready for submission by end of year.

| Planned Date | Summer 2007 | Winter 2008 | Summer 2008 | Winter 2009 | Summer 2009 |
| --- | --- | --- | --- | --- | --- |
| Task | Outline | Rough Draft/PAR | Final Draft | Submission | Review Resolved |
| Actual | On Schedule | On Schedule |  |  |  |
| Detail |  | PAR 1651 |  |  |  |

15.09.03.05:  Task Force on Insulator Contamination Testing and Dielectric Aging Performance.

Chair:  Dr. Anibal de la O Lavalle

The task force will be meeting this afternoon.  A draft is underway.

| Planned Date | Summer 2007 | Winter 2008 | Summer 2008 | Winter 2009 | Summer 2009 |
| --- | --- | --- | --- | --- | --- |
| Task | Outline | Rough Draft/PAR | Final Draft | Submission | Review Resolved |
| Actual | Late | Outline |  |  |  |

Dr. Kumosa –  Began his research in 1993 with funding from WAPA and BPA in conjunction with EPRI.  The work was concentrated on brittle fracture.  This work was prompted by WAPA failures on a 345 kV line.  Additional PG&E failures in 1996 on a 500 kV line added emphasis.  Over 20 papers have been published in the last 5 years – most within DEIS.  Failures can occur within a few months to a few years.  The WAPA line failed due to insufficient sealing of the end fittings and also to overloading of the insulators, probably during proof testing.  The PG&E failures were due to nitric acid formed in service due to corona discharges, ozone and moisture. This implies that field strength is critical to the failure mechanism.  Water droplet corona on the surface and enter the end fittings with nitric acid formed due to the field.  With weak acid concentration the solution can access the rod and generate partial discharges internally, with multiple transverse fracture surfaces.  Longitudinal cracks above the hardware act to magnify the fields and can generate partial discharge.  FTIR analyses have found nitrates and nitric acid on the surfaces of brittle fractures.  The acids seem to be most concentrated at the interface of the polymer sheath and the fiberglass rod.  Polymers that absorb moisture quickly and in higher percentages are more susceptible to brittle fracture.  ECR high seed sustains one to two orders of magnitude higher fiber failures  than ECR low seed.  Polyesters have the highest damage rate, followed by epoxies and then vinyl esters.  Water diffusion tests (which change the chemistry) indicated that high seed count glass can affect the water diffusion test results for various rod types by permitting higher leakage currents.  As a function of moisture absorbed, the ECR high seed glass rods conducted currents an order of magnitude higher than similar absorptions for low seed glass.

Excessively crimped parts can break as a result.  But there is no mirror zone.   Appropriately grading stresses during crimping can be advantageous.

Dr. Kumosa is starting new research on the Structural Integrity of ACCC Conductors.

15.09.04.01:  Guidelines for in-Service Classification of NCI Damage

Chair:  Tony Carreira

Mr. Carreira noted that the interest in the original plan was low.  He’s approached ESMOL to get their participation and will attempt to build a tool for evaluation of insulator condition. This might be coordinated with test equipment builders.

| Planned Date | Winter 2008 | Summer 2008 | Winter 2009 | Summer 2009 | Winter 2010 |
| --- | --- | --- | --- | --- | --- |
| Task | Outline | Rough Draft/PAR | Final Draft | Submission | Review Resolved |
| Actual |  |  |  |  |  |

15.09.04.02: Task Force on Corona Testing of Hardware & Insulators

Chair: Dr. John Kuffel

Dr. Kuffel routed a draft for comments and received a number.  Once those comments are resolved, it will be published.  TP&C has also expressed an interest.

| Planned Date | Summer 2007 | Winter 2008 | Summer 2008 |
| --- | --- | --- | --- |
| Task | PAR Approved | Paper Submitted | Review Resolved |
| Actual | ??? |  |  |

15.09.09.03:  Icing Test Methods and Mitigation Techniques

Chair:  Dr. Masoud Farzaneh

Dr. Farzaneh discussed the 5 position papers published to date.  His TF is preparing a guide regarding selection and testing of insulators for freezing conditions.  Atmospheric ice is the focus of this group.  The scope concerns both AC and DC voltages.  They have prepared a final draft.  This is a joint TF of DEIS and PES.  They are planning a DEIS in October in Quebec City and will finalize the paper by that point.   When this is done, a selection paper may be prepared.

| Planned Date | Summer 2006 | Winter 2007 | Summer 2007 | Winter 2008 | Summer 2008 |
| --- | --- | --- | --- | --- | --- |
| Task | Joint TF | Outline | 1st Draft | 2nd Draft | Final Draft |
| Actual |  |  |  |  |  |

15.09.09.04:  High Temperature Conductor Effects on Ceramic and Non-Ceramic Insulator Performance

Chair:  Jack Varner.

Mr. Varner is working with EPRI to assemble data for a paper regarding NCIs.  Information has been submitted by MPS, NEETRAC, NGK and HPS.  A copy of a Cigre study has also been obtained.  This will be compiled and a draft prepared.

| Planned Date | Summer 2007 | Winter 2008 | Summer 2008 | Winter 2009 | Summer 2009 |
| --- | --- | --- | --- | --- | --- |
| Task | Outline | Rough Draft/PAR | Final Draft | Submission | Review Resolved |
| Actual | On Schedule |  |  |  |  |

15.09.06.06:  Review of Mechanism that Affects the In-Service Strength and End-of-Life Decisions for Ceramic and Glass Insulators

Chair:  Ezio del Bello

Not present.

| Planned Date | Summer 2007 | Winter 2008 | Summer 2009 | Winter 2009 | Summer 2009 |
| --- | --- | --- | --- | --- | --- |
| Task | Outline | Rough Draft/PAR | Final Draft | Submission | Review Resolved |
| Actual | On Schedule |  |  |  |  |

15.09.09.08:  Task Force for a Recommended Practice on Insulator Loading

Chair:  Tony Baker

A TF has been assembled and the plan is to have a final paper completed by Summer 2009.  If it’s not a standard, they may not need a PAR.

| Planned Date | Summer 2008 | Winter 2009 | Summer 2009 | Winter 2010 | Summer 2010 |
| --- | --- | --- | --- | --- | --- |
| Task | Outline | Rough Draft/PAR | Final Draft | Submission | Review Resolved |
| Actual | On Schedule |  |  |  |  |

TF for Insulators 101

Chair:  Tom Grisham

This TF was formed to help generate more interest in the Insulator Performance and Applications WG.  The objective is to summarize ceramic insulators and Non-ceramics in terms of their history, design and application performance.  Questions exist regarding the need for the task force.

| Planned Date | Summer 2008 | Winter 2009 | Summer 2009 | Winter 2010 | Summer 2010 |
| --- | --- | --- | --- | --- | --- |
| Task | Outline | Rough Draft/PAR | Final Draft | Submission | Review Resolved |
| Actual | On Schedule |  |  |  |  |

Jack Varner/Frank Lambert – Super Hydrophobicity.   In 2006, a nano-technological approach to super hydrophobicity was developed.  Mr. Lambert noted that they’re using a “lotus-effect” surface for maintaining contact angles greater than 150.  The coating that they are applying will help to inhibit tracking damage to the substrate.  The material has been applied to SR, EVA and EP polymers.  The material can be applied by spraying, brushing or dipping.

Insulators with this coating have been installed in Mississippi near a chemical plant.  Ohio Brass silicone insulators were used for the evaluation.  They were sprayed with the solution before installation.  The guy wires and hardware used on this line section are changed every six weeks.

“Development of New-Type Outdoor Terminations Using Composite Insulator” – presented by M. Tanigochi.   The development was prompted by the high cost of land in Japan.  They developed a termination to be used on the tower and connected to underground cable run through the tower body.  Additionally, they were concerned about weight and clearances.  Vertical installations did not offer adequate clearance.  They developed a horizontal termination to avoid clearance issues.  Normally developed terminations use an air chamber to compensate for the expansion and contraction of the silicone oil.  They replaced the silicone oil with SF6 gas.   This allowed the overall weight of the assembly to be cut in half.  All testing was passed.  Some minor shape modifications improved the electrical performance.

15.09.09:  Insulator Performance and Applications WG:

Chair:  Allen Bernstorf

Panel Sessions:   The following ideas were presented along with the schedule.

| Topic | Moderator | Members | Paper Due Date | Target Panel Date |
| --- | --- | --- | --- | --- |
| Strength Ratings | Andrew Schwalm |  | ???? | ???? |
| Fiberglass Rod Failure Mechanisms | Dr. Andrew Phillips |  | 12/10/09 | Summer 2009 |
| Live Line Maintenance | Tony Carreira | Jack Varner |  | ESMO 2010 |
| High Temperature Systems (insulators, conductor and hardware) | Jack Varner |  |  | T & D 2010 |
| Line Arresters and Reliability | Dr. Bill Chisholm |  |  | 2010 T & D |

Standards:

| Number | Name | Date | Action |
| --- | --- | --- | --- |
| 1572 | IEEE Guide for Application of Composite Line Post Insulators | 2004 | Merge the two? |
| 987 | IEEE Guide for Application of Composite Insulators | 2001 |  |

Tutorials:

New Business:

Next Meeting and Meeting Room Requests:

The next meeting will be held in Orlando, FL, from January 11-15, 2009.   Task Forces requesting time and meeting rooms for individual meetings during that event include:

- 15.09.03.01 – TF on Aging of Outdoor Insulator Dielectric Materials – Dr. John Kuffel – W09

- 15.09.03.04 – TF on Bird Related Outages – Dr. Raji Sundararajan – S09

Adjournment:

The meeting was adjourned at 11:45 a.m.

Respectfully submitted,

R. Allen Bernstorf

Notable Dates:

| Date | Deadline | Event |
| --- | --- | --- |