## Sheet1
Title | TVA Tupelo-Oxford | [5 empty] | Program Path |  | d:\flash\flash.exe
GFD [per sq km] | 6 | [5 empty] | Scratch Input File |  | d:\flash\testxl.dat
Span [m] | 195 | [5 empty] | Scratch Output File |  | d:\flash\testxl.out
Conductors | [7 empty] | Shield Wires
Diameter [mm] | 14.3 |  | # Bundled |  | 1 |  |  | Diameter [mm] | 9.5
Sag [m] | 1.5 |  | Spacing [mm] |  | 0 |  |  | Sag [m] | 0.3
Index | X [m] | Y [m] | SI [m] | kV | Angle | AC/DC? |  | Index | X [m] | Y [m]
1 | -3.81 | 9.63 | 1.91 | 161 | 0 | ac |  | 1 | -2.08 | 12.73
2 | 0 | 9.63 | 1.91 | 161 | 120 | ac |  | 2 | 2.08 | 12.73
3 | 3.81 | 9.63 | 1.91 | 161 | 240 | ac
4 | [7 empty] | Exposed Conductors |  |  | Shielding Angles
5 | [7 empty] | Index | Conductor | Shield Wire | Required | Actual
6 | [7 empty] | 1 | 1 | 1 | 39.7 | 23.92
7 | [7 empty] | 2 | 3 | 2 | 39.7 | 23.92
8 | [7 empty] | 3
9 | [7 empty] | 4
10
11 | [7 empty] | Footing Resistances |  | Flashover Rates
12 | [7 empty] | Percentage (*) | Ohms | Backflash | 2.95 | /100 km/yr
[8 empty] | 10 | 38.5 | Shielding Failure | 0 | /100 km/yr
Tower Model |  |  |  | Do Not Edit: |  |  |  | 90 | 38.5 | Total | 2.95 | /100 km/yr
Height | 13.11 | [m] |  | 1 - Cone
Lead Diameter | 0.2 | [m] |  | 2 - H Frame
Lead Separation | 7.6 | [m] |  | 3 - Cylinder
-not used- | 0 | [m] |  | 4 - Waist
-not used- | 0 | [m]
Version 1.81 - July 2001
[8 empty] | Check Sum: | 100
(*) can use percentage, number of towers, or line segment lengths